## Master
#Modbus Slave Nodes
#Bezeichnung der Modbus Slave Nodes

## Slave
#Modbus Slave
#Generelle Informationen
mySlaveDeviceType=3
mySlaveDeviceAddress=16

## Funktionen
BaMo MODBUS | Function | Sub-function | Supported | Note
Data access | Read Coils |  | Yes
| Read Discrete Inputs |  | Yes
| Read Holding Registers |  | Yes
| Read Input Register |  | Yes
| Write Single Coil |  | Yes
| Write Single Register |  | Yes
| Write Multiple Coils |  | Yes
| Write Multiple Registers |  | Yes
| Read/Write Multiple Registers |  | No
| Mask Write Register |  | No
| Read FIFO queue |  | No
Diagnostics | Read Exception Status |  | No
| Diagnostic | Return Query Data | Yes | loopback
|  | Restart Communications Option | No
|  | Return Diagnostic Register | No | diagnostic register to be defined
|  | Change ASCII Input Delimiter | No
|  | Force Listen Only Mode | Yes | no response to requests
|  | Clear Counters and Diagnostic Register | Yes
|  | Return Bus Message Count | Yes | Received frames total (Req, ack)
|  | Return Bus Communication Error Count | Yes | Received frames with CRC error
|  | Return Bus Exception Error Count | Yes | Anzahl exception responses von Slave
|  | Return Slave Message Count | Yes | Anzahl CRC-ok requests an slave incl. broadcasts.
|  | Return Slave No Response Count | Yes | Anzahl CRC-ok Req ohne response
|  | Return Slave NAK Count | Yes | Anzahl NAK exception responses
|  | Return Slave Busy Count | No
|  | Return Bus Character Overrun Count | No
|  | Clear Overrun Counter and Flag | No
| Get Com event counter |  | No | Status (idle, busy), com event counter
| Get Com Event Log |  | No | Status, com event counter, bus message count, 0..64 event bytes ( Receive Event, Send Event, Entered Listen Only Mode,Initiated Communication Restart
| Report Slave ID |  | No | slave ID, status, additional data
| Read device Identification |  | No
File record access | Read File record |  | No
| Write File record |  | No
Other | Encapsulated Interface Transport |  | No

## InputRegister
#Name | Short-Name | MB-Adr (hex) | Index | Einheit | Type | Default
#Ladezustand
Spezifizierte Batteriekapazitaet | DESIGN_CAPACITY | 1 | 0 | 10 mAh | unsigned | 0
Berechnete kompensierte Gesamtbatteriekapazitaet | FULL_CHARGE_CAPACITY | 2 | 1 | 10 mAh | unsigned | 0
Unkompensierte Gesamtkapazitaet | FULL_AVAILABLE_CAPACITY | 3 | 2 | 10 mAh | unsigned | 0
Momentaner Ladezustand in % von der berechneten Gesamtkapazitaet | STATE_OF_CHARGE | 4 | 3 | % | unsigned | 0
Momentan verfuegbare kompensierte Batteriekapazitaet | REMAINING_CAPACITY | 5 | 4 | 10 mAh | unsigned | 0
Momentan verfuegbare unkompensierte Batteriekapazitaet | NOMINAL_AVAILABLE_CAPACITY | 6 | 5 | 10 mAh | unsigned | 0
Momentan verfuegbare Restenergie | AVAILABLE_ENERGY | 7 | 6 | Wh | unsigned | 0
Momentan verfuegbare Restleistung | AVAILABLE_POWER | 8 | 7 | W | unsigned | 0
Restlaufzeit bei bestimmtem Entladestrom | ATRATE_TIME_TO_EMPTY | 9 | 8 | min | unsigned | 0
Restlaufzeit bei momentanem Entladestrom | TIME_TO_EMPTY | 10 | 9 | min | unsigned | 0
Restlaufzeit bei maximalem Entladestrom | MAX_LOAD_TIME_TO_EMPTY | 11 | 10 | min | unsigned | 0
Restlaufzeit bei Standby-Entladestrom | STANDBY_TIME_TO_EMPTY | 12 | 11 | min | unsigned | 0
Restlaufzeit bei durchschnittlicher Entladeleistung | TIME_TO_EMPTY_AT_CONSTANT_POWER | 13 | 12 | min | unsigned | 0
Restladezeit bei durchschnittlichem Entladestrom | TIME_TO_FULL | 14 | 13 | min | unsigned | 0
Spezifizierte Batteriekapazitaet vs. Berechnete Gesamtbatteriekapazitaet | STATE_OF_HEALTH | 15 | 14 | % | unsigned | 0
Statusinformationen vom TI BQ34Z110 | CONTROL_STATUS | 16 | 15 | # | unsigned | 0
#Spannung
Aktuelle Gesamtbatteriespannung | VOLTAGE | 17 | 16 | mV | unsigned | 0
Spannung Zelle 1 | VOLTAGE_CELL_1 | 18 | 17 | 0.1 mV | unsigned | 0
Spannung Zelle 2 | VOLTAGE_CELL_2 | 19 | 18 | 0.1 mV | unsigned | 0
Spannung Zelle 3 | VOLTAGE_CELL_3 | 20 | 19 | 0.1 mV | unsigned | 0
Spannung Zelle 4 | VOLTAGE_CELL_4 | 21 | 20 | 0.1 mV | unsigned | 0
Spannung Zelle 5 | VOLTAGE_CELL_5 | 22 | 21 | 0.1 mV | unsigned | 0
Spannung Zelle 6 | VOLTAGE_CELL_6 | 23 | 22 | 0.1 mV | unsigned | 0
Spannung Zelle 7 | VOLTAGE_CELL_7 | 24 | 23 | 0.1 mV | unsigned | 0
Spannung Zelle 8 | VOLTAGE_CELL_8 | 25 | 24 | 0.1 mV | unsigned | 0
Spannung Zelle 9 | VOLTAGE_CELL_9 | 26 | 25 | 0.1 mV | unsigned | 0
Spannung Zelle 10 | VOLTAGE_CELL_10 | 27 | 26 | 0.1 mV | unsigned | 0
Spannung Zelle 11 | VOLTAGE_CELL_11 | 28 | 27 | 0.1 mV | unsigned | 0
Spannung Zelle 12 | VOLTAGE_CELL_12 | 29 | 28 | 0.1 mV | unsigned | 0
Spannung Zelle 13 | VOLTAGE_CELL_13 | 30 | 29 | 0.1 mV | unsigned | 0
Spannung Zelle 14 | VOLTAGE_CELL_14 | 31 | 30 | 0.1 mV | unsigned | 0
Spannung Zelle 15 | VOLTAGE_CELL_15 | 32 | 31 | 0.1 mV | unsigned | 0
Spannung Zelle 16 | VOLTAGE_CELL_16 | 33 | 32 | 0.1 mV | unsigned | 0
Spannung Zelle 17 | VOLTAGE_CELL_17 | 34 | 33 | 0.1 mV | unsigned | 0
Spannung Zelle 18 | VOLTAGE_CELL_18 | 35 | 34 | 0.1 mV | unsigned | 0
Spannung Zelle 19 | VOLTAGE_CELL_19 | 36 | 35 | 0.1 mV | unsigned | 0
Spannung Zelle 20 | VOLTAGE_CELL_20 | 37 | 36 | 0.1 mV | unsigned | 0
Spannung Zelle 21 | VOLTAGE_CELL_21 | 38 | 37 | 0.1 mV | unsigned | 0
Spannung Zelle 22 | VOLTAGE_CELL_22 | 39 | 38 | 0.1 mV | unsigned | 0
Spannung Zelle 23 | VOLTAGE_CELL_23 | 40 | 39 | 0.1 mV | unsigned | 0
Spannung Zelle 24 | VOLTAGE_CELL_24 | 41 | 40 | 0.1 mV | unsigned | 0
Empfohlene Ladespannung [mV] | CHARGE_VOLTAGE | 42 | 41 | mV | unsigned | 0
#Strom
Durchschnittlicher Lade- bzw. Entladestrom | AVERAGE_CURRENT | 43 | 42 | 10 mA | signed | 0
Momentaner Lade- bzw. Entladestrom | CURRENT | 44 | 43 | 10 mA | signed | 0
Maximaler Entladestrom im aktuellen Ladezyklus | MAX_LOAD_CURRENT | 45 | 44 | 10 mA | signed | 0
Standby Strom | STANDBY_CURRENT | 46 | 45 | 10 mA | signed | 0
Durchschnittliche Entladeleistung | AVERAGE_POWER | 47 | 46 | W | unsigned | 0
Empfohlener Ladestrom | CHARGE_CURRENT | 48 | 47 | 10 mA | signed | 0
Schaetzung des Selbstentladestroms | SELF_DISCHARGE_CURRENT | 49 | 48 | 10 mA | signed | 0
Anzahl Entladezyklen | CYCLE_COUNT | 50 | 49 | # | unsigned | 0
#Temperatur
Temperaturmesswert NTC 1 (PC 0) | NTC_PC_0 | 51 | 50 | 0.01°C | signed | 0
Temperaturmesswert NTC 2 (PC 1) | NTC_PC_1 | 52 | 51 | 0.01°C | signed | 0
Temperaturmesswert NTC 3 (LTC 0) | NTC_LTC_0 | 53 | 52 | 0.01°C | signed | 0
Temperaturmesswert NTC 4 (LTC 1) | NTC_LTC_1 | 54 | 53 | 0.01°C | signed | 0
Temperaturmesswert NTC 5 (LTC 2) | NTC_LTC_2 | 55 | 54 | 0.01°C | signed | 0
Temperaturmesswert NTC 6 (BQZ) | NTC_BQZ | 56 | 55 | 0.01°C | signed | 0
#LTC6804
Gesamtspannung | LTC6804_SOC_1 | 57 | 56 | mV | unsigned | 0
Gesamtspannung | LTC6804_SOC_2 | 58 | 57 | mV | unsigned | 0
Analogspannung | LTC6804_VA_1 | 59 | 58 | 0.1 mV | unsigned | 0
Analogspannung | LTC6804_VA_2 | 60 | 59 | 0.1 mV | unsigned | 0
Digitalspannung | LTC6804_VD_1 | 61 | 60 | 0.1 mV | unsigned | 0
Digitalspannung | LTC6804_VD_2 | 62 | 61 | 0.1 mV | unsigned | 0
Referenzspannung U_ref2 | LTC6804_REF2_1 | 63 | 62 | 0.1 mV | unsigned | 0
Referenzspannung U_ref2 | LTC6804_REF2_2 | 64 | 63 | 0.1 mV | unsigned | 0
#DEVICE information
Manufacturer | DEV_MANUFACTURER | 65 | 64 | ASCII | unsigned | 83
Manufacturer 1 | DEV_MANUFACTURER_1 | 66 | 65 | ASCII | unsigned | 97
Manufacturer 2 | DEV_MANUFACTURER_2 | 67 | 66 | ASCII | unsigned | 117
Manufacturer 3 | DEV_MANUFACTURER_3 | 68 | 67 | ASCII | unsigned | 116
Manufacturer 4 | DEV_MANUFACTURER_4 | 69 | 68 | ASCII | unsigned | 101
Manufacturer 5 | DEV_MANUFACTURER_5 | 70 | 69 | ASCII | unsigned | 114
Manufacturer 6 | DEV_MANUFACTURER_6 | 71 | 70 | ASCII | unsigned | 32
Manufacturer 7 | DEV_MANUFACTURER_7 | 72 | 71 | ASCII | unsigned | 76
Manufacturer 8 | DEV_MANUFACTURER_8 | 73 | 72 | ASCII | unsigned | 116
Manufacturer 9 | DEV_MANUFACTURER_9 | 74 | 73 | ASCII | unsigned | 100
Manufacturer 10 | DEV_MANUFACTURER_10 | 75 | 74 | ASCII | unsigned | 0
Device Name | DEV_NAME | 76 | 75 | ASCII | unsigned | 66
Device Name 1 | DEV_NAME_1 | 77 | 76 | ASCII | unsigned | 97
Device Name 2 | DEV_NAME_2 | 78 | 77 | ASCII | unsigned | 77
Device Name 3 | DEV_NAME_3 | 79 | 78 | ASCII | unsigned | 111
Device Name 4 | DEV_NAME_4 | 80 | 79 | ASCII | unsigned | 0
Device Type | DEV_TYPE | 81 | 80 | # | unsigned | 1
Release Version | VERSION_RELEASE | 82 | 81 | # | unsigned | 1
Major Version | VERSION_MAJOR | 83 | 82 | # | unsigned | 0
Minor Version | VERSION_MINOR | 84 | 83 | # | unsigned | 1
Build | BUILD | 85 | 84 | ASCII | unsigned | 0
Build 1 | BUILD_1 | 86 | 85 | ASCII | unsigned | 0
Build 2 | BUILD_2 | 87 | 86 | ASCII | unsigned | 0
Build 3 | BUILD_3 | 88 | 87 | ASCII | unsigned | 0
Build 4 | BUILD_4 | 89 | 88 | ASCII | unsigned | 0
Build 5 | BUILD_5 | 90 | 89 | ASCII | unsigned | 0
Build 6 | BUILD_6 | 91 | 90 | ASCII | unsigned | 0
Build 7 | BUILD_7 | 92 | 91 | ASCII | unsigned | 0
Build 8 | BUILD_8 | 93 | 92 | ASCII | unsigned | 0
Build 9 | BUILD_9 | 94 | 93 | ASCII | unsigned | 0

## HoldingRegister
#Name | EEPROM | Master-Mirror | Short-Name | MB-Adr (dezimal) | MB-Adr (hex) | Index | Einheit | Type | Min | Max | Default
#Konfiguration
Firmware Version Application | 0 | 0 | FW_VERSION | 0 | 0 | 0 | char | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_1 | 1 | 1 | 1 | char | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_2 | 2 | 2 | 2 | char | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_3 | 3 | 3 | 3 | char | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_4 | 4 | 4 | 4 | char | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_5 | 5 | 5 | 5 | char | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_6 | 6 | 6 | 6 | char | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_7 | 7 | 7 | 7 | char | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_8 | 8 | 8 | 8 | char | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_9 | 9 | 9 | 9 | char | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_10 | 10 | A | 10 | char | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_11 | 11 | B | 11 | char | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_12 | 12 | C | 12 | char | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_13 | 13 | D | 13 | char | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_14 | 14 | E | 14 | char | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_15 | 15 | F | 15 | char | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_16 | 16 | 10 | 16 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_17 | 17 | 11 | 17 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_18 | 18 | 12 | 18 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_19 | 19 | 13 | 19 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_20 | 20 | 14 | 20 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_21 | 21 | 15 | 21 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_22 | 22 | 16 | 22 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_23 | 23 | 17 | 23 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_24 | 24 | 18 | 24 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_25 | 25 | 19 | 25 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_26 | 26 | 1A | 26 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_27 | 27 | 1B | 27 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_28 | 28 | 1C | 28 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_29 | 29 | 1D | 29 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_30 | 30 | 1E | 30 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_31 | 31 | 1F | 31 | - | unsigned | 0 | 65535 | 0
Hardware Version | 0 | 0 | HW_VERSION | 48 | 30 | 32 | char | unsigned | 0 | 65535 | 0
Hardware Version | 0 | 0 | HW_VERSION_1 | 49 | 31 | 33 | char | unsigned | 0 | 65535 | 0
Hardware Version | 0 | 0 | HW_VERSION_2 | 50 | 32 | 34 | char | unsigned | 0 | 65535 | 0
Hardware Version | 0 | 0 | HW_VERSION_3 | 51 | 33 | 35 | char | unsigned | 0 | 65535 | 0
Hardware Version | 0 | 0 | HW_VERSION_4 | 52 | 34 | 36 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL | 53 | 35 | 37 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_1 | 54 | 36 | 38 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_2 | 55 | 37 | 39 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_3 | 56 | 38 | 40 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_4 | 57 | 39 | 41 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_5 | 58 | 3A | 42 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_6 | 59 | 3B | 43 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_7 | 60 | 3C | 44 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_8 | 61 | 3D | 45 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_9 | 62 | 3E | 46 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_10 | 63 | 3F | 47 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_11 | 64 | 40 | 48 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_12 | 65 | 41 | 49 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_13 | 66 | 42 | 50 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_14 | 67 | 43 | 51 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_15 | 68 | 44 | 52 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_16 | 69 | 45 | 53 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_17 | 70 | 46 | 54 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_18 | 71 | 47 | 55 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_19 | 72 | 48 | 56 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_20 | 73 | 49 | 57 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_21 | 74 | 4A | 58 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_22 | 75 | 4B | 59 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_23 | 76 | 4C | 60 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_24 | 77 | 4D | 61 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_25 | 78 | 4E | 62 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_26 | 79 | 4F | 63 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_27 | 80 | 50 | 64 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_28 | 81 | 51 | 65 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_29 | 82 | 52 | 66 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_30 | 83 | 53 | 67 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_31 | 84 | 54 | 68 | - | unsigned | 0 | 65535 | 0
eepromVersion | 1 | 0 | EEPROM_VERSION | 255 | FF | 69 | - | unsigned | 0 | 65535 | 43776
Device Type | 0 | 1 | DEVICE_TYPE | 256 | 100 | 70 | - | unsigned | 0 | 65535 | 3
(Random/Set) Modbus Address | 1 | 0 | MODBUS_ADDRESS | 257 | 101 | 71 | - | unsigned | 0 | 65535 | 16
Modbus Timeout | 1 | 0 | MODBUS_TIMEOUT_LIGHTMEASURING_MULTI_FAKTOR | 258 | 102 | 72 | - | unsigned | 0 | 65535 | 20
Command - Devicetype | 0 | 0 | MODBUS_COMMAND | 259 | 103 | 73 | - | unsigned | 0 | 65535 | 0
Write SN/BIL/DATE/Order Code = BEEF - Erase // FLASH = DEAD | 0 | 0 | WRITE_MANUFACTURER_INFO | 512 | 200 | 74 | - | unsigned | 0 | 65535 | 0
Manufacturer Serialnumber | 0 | 0 | SERIAL_NUMBER | 528 | 210 | 75 | char | unsigned | 0 | 65535 | 0
Manufacturer Serialnumber | 0 | 0 | SERIAL_NUMBER_1 | 529 | 211 | 76 | char | unsigned | 0 | 65535 | 0
Manufacturer Serialnumber | 0 | 0 | SERIAL_NUMBER_2 | 530 | 212 | 77 | char | unsigned | 0 | 65535 | 0
Manufacturer Serialnumber | 0 | 0 | SERIAL_NUMBER_3 | 531 | 213 | 78 | char | unsigned | 0 | 65535 | 0
Manufacturer Serialnumber | 0 | 0 | SERIAL_NUMBER_4 | 532 | 214 | 79 | char | unsigned | 0 | 65535 | 0
Manufacturer Serialnumber | 0 | 0 | SERIAL_NUMBER_5 | 533 | 215 | 80 | char | unsigned | 0 | 65535 | 0
Manufacturer Serialnumber | 0 | 0 | SERIAL_NUMBER_6 | 534 | 216 | 81 | char | unsigned | 0 | 65535 | 0
Manufacturer Serialnumber | 0 | 0 | SERIAL_NUMBER_7 | 535 | 217 | 82 | char | unsigned | 0 | 65535 | 0
Manufacturer Hardware Version (BOM) | 0 | 0 | HW_BOM_VERSION | 536 | 218 | 83 | char | unsigned | 0 | 65535 | 0
Manufacturer Hardware Version (BOM) | 0 | 0 | HW_BOM_VERSION_1 | 537 | 219 | 84 | char | unsigned | 0 | 65535 | 0
Manufacturer Hardware Version (BOM) | 0 | 0 | HW_BOM_VERSION_2 | 538 | 21A | 85 | char | unsigned | 0 | 65535 | 0
Manufacturer Hardware Version (BOM) | 0 | 0 | HW_BOM_VERSION_3 | 539 | 21B | 86 | char | unsigned | 0 | 65535 | 0
Manufacturer Hardware Version (BOM) | 0 | 0 | HW_BOM_VERSION_4 | 540 | 21C | 87 | char | unsigned | 0 | 65535 | 0
Manufacturer Hardware Version (BOM) | 0 | 0 | HW_BOM_VERSION_5 | 541 | 21D | 88 | char | unsigned | 0 | 65535 | 0
Manufacturer Hardware Version (BOM) | 0 | 0 | HW_BOM_VERSION_6 | 542 | 21E | 89 | char | unsigned | 0 | 65535 | 0
Manufacturer Hardware Version (BOM) | 0 | 0 | HW_BOM_VERSION_7 | 543 | 21F | 90 | char | unsigned | 0 | 65535 | 0
Manufacturer Date/Time | 0 | 0 | DATE | 544 | 220 | 91 | char | unsigned | 0 | 65535 | 0
Manufacturer Date/Time | 0 | 0 | DATE_1 | 545 | 221 | 92 | char | unsigned | 0 | 65535 | 0
Manufacturer Date/Time | 0 | 0 | DATE_2 | 546 | 222 | 93 | char | unsigned | 0 | 65535 | 0
Manufacturer Date/Time | 0 | 0 | DATE_3 | 547 | 223 | 94 | char | unsigned | 0 | 65535 | 0
Manufacturer Date/Time | 0 | 0 | DATE_4 | 548 | 224 | 95 | char | unsigned | 0 | 65535 | 0
Manufacturer Date/Time | 0 | 0 | DATE_5 | 549 | 225 | 96 | char | unsigned | 0 | 65535 | 0
Manufacturer Date/Time | 0 | 0 | DATE_6 | 550 | 226 | 97 | char | unsigned | 0 | 65535 | 0
Manufacturer Date/Time | 0 | 0 | DATE_7 | 551 | 227 | 98 | char | unsigned | 0 | 65535 | 0
Regent Item Number | 0 | 0 | REGENT_ITEM_NUMBER | 552 | 228 | 99 | char | unsigned | 0 | 65535 | 0
Regent Item Number | 0 | 0 | REGENT_ITEM_NUMBER_1 | 553 | 229 | 100 | char | unsigned | 0 | 65535 | 0
Regent Item Number | 0 | 0 | REGENT_ITEM_NUMBER_2 | 554 | 22A | 101 | char | unsigned | 0 | 65535 | 0
Regent Item Number | 0 | 0 | REGENT_ITEM_NUMBER_3 | 555 | 22B | 102 | char | unsigned | 0 | 65535 | 0
Regent Item Number | 0 | 0 | REGENT_ITEM_NUMBER_4 | 556 | 22C | 103 | char | unsigned | 0 | 65535 | 0
Regent Item Number | 0 | 0 | REGENT_ITEM_NUMBER_5 | 557 | 22D | 104 | char | unsigned | 0 | 65535 | 0
Regent Item Number | 0 | 0 | REGENT_ITEM_NUMBER_6 | 558 | 22E | 105 | char | unsigned | 0 | 65535 | 0
Regent Item Number | 0 | 0 | REGENT_ITEM_NUMBER_7 | 559 | 22F | 106 | char | unsigned | 0 | 65535 | 0
IR Testresult (selftest) | 0 | 0 | IR_TESTRESULT | 4112 | 1010 | 107 | - | unsigned | 0 | 65535 | 1
US Testresult (selftest) | 0 | 0 | US_TESTRESULT1 | 4113 | 1011 | 108 | - | unsigned | 0 | 65535 | 65535
US Testresult (selftest) | 0 | 0 | US_TESTRESULT2 | 4114 | 1012 | 109 | - | unsigned | 0 | 65535 | 255
US Testresult channel 0 | 0 | 0 | US_CHANNEL_0 | 4115 | 1013 | 110 | - | unsigned | 0 | 65535 | 0
US Testresult channel 1 | 0 | 0 | US_CHANNEL_1 | 4116 | 1014 | 111 | - | unsigned | 0 | 65535 | 0
US Testresult channel 2 | 0 | 0 | US_CHANNEL_2 | 4117 | 1015 | 112 | - | unsigned | 0 | 65535 | 0
US Testresult channel 3 | 0 | 0 | US_CHANNEL_3 | 4118 | 1016 | 113 | - | unsigned | 0 | 65535 | 0
Reduction Table (local) | 1 | 0 | REDUCTION_TABLE_START | 4128 | 1020 | 114 | - | unsigned | 0 | 65535 | 34
Reduction Table (0m < X < 1m) | 1 | 0 | REDUCTION_TABLE_1 | 4129 | 1021 | 115 | - | unsigned | 0 | 65535 | 34
Reduction Table (1m < X < 2m) | 1 | 0 | REDUCTION_TABLE_2 | 4130 | 1022 | 116 | - | unsigned | 0 | 65535 | 34
Reduction Table (2m < X < 3m) | 1 | 0 | REDUCTION_TABLE_3 | 4131 | 1023 | 117 | - | unsigned | 0 | 65535 | 34
Reduction Table … | 1 | 0 | REDUCTION_TABLE_4 | 4132 | 1024 | 118 | - | unsigned | 0 | 65535 | 34
Reduction Table … | 1 | 0 | REDUCTION_TABLE_5 | 4133 | 1025 | 119 | - | unsigned | 0 | 65535 | 34
Reduction Table … | 1 | 0 | REDUCTION_TABLE_6 | 4134 | 1026 | 120 | - | unsigned | 0 | 65535 | 67
Reduction Table … | 1 | 0 | REDUCTION_TABLE_7 | 4135 | 1027 | 121 | - | unsigned | 0 | 65535 | 67
Reduction Table … | 1 | 0 | REDUCTION_TABLE_8 | 4136 | 1028 | 122 | - | unsigned | 0 | 65535 | 67
Reduction Table … | 1 | 0 | REDUCTION_TABLE_9 | 4137 | 1029 | 123 | - | unsigned | 0 | 65535 | 67
Reduction Table … | 1 | 0 | REDUCTION_TABLE_10 | 4138 | 102A | 124 | - | unsigned | 0 | 65535 | 67
Reduction Table … | 1 | 0 | REDUCTION_TABLE_11 | 4139 | 102B | 125 | - | unsigned | 0 | 65535 | 100
Reduction Table … | 1 | 0 | REDUCTION_TABLE_12 | 4140 | 102C | 126 | - | unsigned | 0 | 65535 | 100
Reduction Table … | 1 | 0 | REDUCTION_TABLE_13 | 4141 | 102D | 127 | - | unsigned | 0 | 65535 | 100
Reduction Table … | 1 | 0 | REDUCTION_TABLE_14 | 4142 | 102E | 128 | - | unsigned | 0 | 65535 | 100
Reduction Table … | 1 | 0 | REDUCTION_TABLE_15 | 4143 | 102F | 129 | - | unsigned | 0 | 65535 | 100
Reduction Table … | 1 | 0 | REDUCTION_TABLE_16 | 4144 | 1030 | 130 | - | unsigned | 0 | 65535 | 100
Reduction Table … | 1 | 0 | REDUCTION_TABLE_17 | 4145 | 1031 | 131 | - | unsigned | 0 | 65535 | 100
Reduction Table (17m < X < 18m) | 1 | 0 | REDUCTION_TABLE_18 | 4146 | 1032 | 132 | - | unsigned | 0 | 65535 | 100
Reduction Table (18m < X < 19m) | 1 | 0 | REDUCTION_TABLE_END | 4147 | 1033 | 133 | - | unsigned | 0 | 65535 | 100
Remain light for additional light | 1 | 0 | REMAIN_LIGHT | 4148 | 1034 | 134 | - | unsigned | 0 | 65535 | 0
ALONEatWORK ID | 1 | 0 | AAW_ID | 4149 | 1035 | 135 | - | unsigned | 0 | 65535 | 0
Time to live | 1 | 0 | TIME_TO_LIVE | 4150 | 1036 | 136 | - | unsigned | 0 | 65535 | 30
Resend time in seconds | 1 | 0 | RESEND_TIME | 4151 | 1037 | 137 | - | unsigned | 0 | 65535 | 2
Maximum supported distance from luminare to luminaire | 1 | 0 | MAX_DISTANCE | 4152 | 1038 | 138 | - | unsigned | 0 | 65535 | 7
Treshold for LOK (lock count) | 1 | 0 | LOCK_COUNT | 4153 | 1039 | 139 | - | unsigned | 0 | 65535 | 50
Init | 1 | 0 | EEPROM_INIT | 4154 | 103A | 140 | - | unsigned | 0 | 65535 | 2
Sniffer mode | 1 | 0 | SNIFFER_MODE | 4155 | 103B | 141 | - | unsigned | 0 | 65535 | 0
IDLE | 1 | 0 | IDLE | 4200 | 1068 | 142 | - | unsigned | 0 | 65535 | 0
ORE | 1 | 0 | ORE | 4201 | 1069 | 143 | - | unsigned | 0 | 65535 | 0
PE | 1 | 0 | PE | 4202 | 106A | 144 | - | unsigned | 0 | 65535 | 0
LBD | 1 | 0 | LBD | 4203 | 106B | 145 | - | unsigned | 0 | 65535 | 0
NE | 1 | 0 | NE | 4204 | 106C | 146 | - | unsigned | 0 | 65535 | 0
FE | 1 | 0 | FE | 4205 | 106D | 147 | - | unsigned | 0 | 65535 | 0
CTS | 1 | 0 | CTS | 4206 | 106E | 148 | - | unsigned | 0 | 65535 | 0
"No-Master" Reset Timeout in seconds | 1 | 0 | NO_MASTER_TIMEOUT | 4207 | 106F | 149 | - | unsigned | 0 | 65535 | 120
Device Reset Counter because of "No-Master" | 1 | 0 | NO_MASTER_RESET_COUNTER | 4208 | 1070 | 150 | - | unsigned | 0 | 65535 | 0
Remote Brightness | 0 | 1 | REMOTE_BRIGHTNESS_VALUE | 4352 | 1100 | 151 | - | unsigned | 0 | 65535 | 0
Remote DALI Value | 0 | 1 | REMOTE_DALI_VALUE | 4353 | 1101 | 152 | - | unsigned | 0 | 65535 | 0
Local Brightness | 0 | 1 | LOCAL_BRIGHTNESS_VALUE | 4354 | 1102 | 153 | - | unsigned | 0 | 65535 | 0
Local DALI Value | 0 | 1 | LOCAL_DALI_VALUE | 4355 | 1103 | 154 | - | unsigned | 0 | 65535 | 0
Error Alone AT Work | 0 | 1 | ERROR_ALONE_AT_WORK | 4356 | 1104 | 155 | - | unsigned | 0 | 65535 | 0
Local LED Color | 0 | 1 | LOCAL_LED_COLOR | 4357 | 1105 | 156 | - | unsigned | 0 | 65535 | 0
Remote LED Color | 0 | 1 | REMOTE_LED_COLOR | 4358 | 1106 | 157 | - | unsigned | 0 | 65535 | 0
Device states | 0 | 0 | DEVICE_STATES | 10008 | 2718 | 158 | - | unsigned | 0 | 65535 | 0
ModBus Error Counters | 0 | 0 | MODBUS_ERRORS | 12288 | 3000 | 159 | - | unsigned | 0 | 65535 | 0
Infrared ID | 0 | 0 | INFRARED_ID | 12289 | 3001 | 160 | - | unsigned | 0 | 65535 | 0
Active Master | 0 | 0 | MASTER_ID | 12290 | 3002 | 161 | - | unsigned | 0 | 65535 | 1
Active Master Brightness | 0 | 0 | MASTER_BRIGHTNESS | 12291 | 3003 | 162 | - | unsigned | 0 | 65535 | 65535
Active Master Reduction | 0 | 0 | MASTER_REDUCTION | 12292 | 3004 | 163 | - | unsigned | 0 | 65535 | 255
ID of the master to verify from the shadow table | 0 | 0 | SHADOW_MASTER_ID | 12293 | 3005 | 164 | - | unsigned | 0 | 65535 | 1
Information of master with id SHADOW_MASTER_ID from the shadow table | 0 | 0 | SHADOW_INFORMATION | 12294 | 3006 | 165 | - | unsigned | 0 | 65535 | 65535
IR CRC errors | 0 | 0 | IR_RX_CRC_ERRORS | 12295 | 3007 | 166 | - | unsigned | 0 | 65535 | 255
IR RX DATA OK | 0 | 0 | IR_RX_DATA_OK | 12296 | 3008 | 167 | - | unsigned | 0 | 65535 | 65535
Get measured 12V | 0 | 0 | MEASURED_12V | 16385 | 4001 | 168 | mV | unsigned | 0 | 65535 | 0
Get measured 5V | 0 | 0 | MEASURED_5V | 16386 | 4002 | 169 | mV | unsigned | 0 | 65535 | 0
Get measured 3_3V | 0 | 0 | MEASURED_3_3V | 16387 | 4003 | 170 | mV | unsigned | 0 | 65535 | 0
Get measured VDDA - 0 = Voltage OK 1 = Voltage not OK | 0 | 0 | MEASURED_VDDA | 16388 | 4004 | 171 | mV | unsigned | 0 | 65535 | 0
Get measured Temperature | 0 | 0 | MEASURED_TEMP | 16389 | 4005 | 172 | C | unsigned | 0 | 65535 | 0
Firmware Update | 0 | 0 | FW_UPDATE | 20480 | 5000 | 173 | - | unsigned | 0 | 65535 | 0
Firmware Update 1 | 0 | 0 | FW_UPDATE_1 | 20481 | 5001 | 174 | - | unsigned | 0 | 65535 | 0
Firmware Update 2 | 0 | 0 | FW_UPDATE_2 | 20482 | 5002 | 175 | - | unsigned | 0 | 65535 | 0
Firmware Update 3 | 0 | 0 | FW_UPDATE_3 | 20483 | 5003 | 176 | - | unsigned | 0 | 65535 | 0
Firmware Update 4 | 0 | 0 | FW_UPDATE_4 | 20484 | 5004 | 177 | - | unsigned | 0 | 65535 | 0
Firmware Update 5 | 0 | 0 | FW_UPDATE_5 | 20485 | 5005 | 178 | - | unsigned | 0 | 65535 | 0
Firmware Update 6 | 0 | 0 | FW_UPDATE_6 | 20486 | 5006 | 179 | - | unsigned | 0 | 65535 | 0
Firmware Update 7 | 0 | 0 | FW_UPDATE_7 | 20487 | 5007 | 180 | - | unsigned | 0 | 65535 | 0
Firmware Update 8 | 0 | 0 | FW_UPDATE_8 | 20488 | 5008 | 181 | - | unsigned | 0 | 65535 | 0
Firmware Update 9 | 0 | 0 | FW_UPDATE_9 | 20489 | 5009 | 182 | - | unsigned | 0 | 65535 | 0
Firmware Update 10 | 0 | 0 | FW_UPDATE_10 | 20490 | 500A | 183 | - | unsigned | 0 | 65535 | 0
Firmware Update 11 | 0 | 0 | FW_UPDATE_11 | 20491 | 500B | 184 | - | unsigned | 0 | 65535 | 0
Firmware Update 12 | 0 | 0 | FW_UPDATE_12 | 20492 | 500C | 185 | - | unsigned | 0 | 65535 | 0
Firmware Update 13 | 0 | 0 | FW_UPDATE_13 | 20493 | 500D | 186 | - | unsigned | 0 | 65535 | 0
Firmware Update 14 | 0 | 0 | FW_UPDATE_14 | 20494 | 500E | 187 | - | unsigned | 0 | 65535 | 0
Firmware Update 15 | 0 | 0 | FW_UPDATE_15 | 20495 | 500F | 188 | - | unsigned | 0 | 65535 | 0
Firmware Update 16 | 0 | 0 | FW_UPDATE_16 | 20496 | 5010 | 189 | - | unsigned | 0 | 65535 | 0
Firmware Update 17 | 0 | 0 | FW_UPDATE_17 | 20497 | 5011 | 190 | - | unsigned | 0 | 65535 | 0
Firmware Update 18 | 0 | 0 | FW_UPDATE_18 | 20498 | 5012 | 191 | - | unsigned | 0 | 65535 | 0
Firmware Update 19 | 0 | 0 | FW_UPDATE_19 | 20499 | 5013 | 192 | - | unsigned | 0 | 65535 | 0
Firmware Update 20 | 0 | 0 | FW_UPDATE_20 | 20500 | 5014 | 193 | - | unsigned | 0 | 65535 | 0
Firmware Update 21 | 0 | 0 | FW_UPDATE_21 | 20501 | 5015 | 194 | - | unsigned | 0 | 65535 | 0
Firmware Update 22 | 0 | 0 | FW_UPDATE_22 | 20502 | 5016 | 195 | - | unsigned | 0 | 65535 | 0
Firmware Update 23 | 0 | 0 | FW_UPDATE_23 | 20503 | 5017 | 196 | - | unsigned | 0 | 65535 | 0
Firmware Update 24 | 0 | 0 | FW_UPDATE_24 | 20504 | 5018 | 197 | - | unsigned | 0 | 65535 | 0
Firmware Update 25 | 0 | 0 | FW_UPDATE_25 | 20505 | 5019 | 198 | - | unsigned | 0 | 65535 | 0
Firmware Update 26 | 0 | 0 | FW_UPDATE_26 | 20506 | 501A | 199 | - | unsigned | 0 | 65535 | 0
Firmware Update 27 | 0 | 0 | FW_UPDATE_27 | 20507 | 501B | 200 | - | unsigned | 0 | 65535 | 0
Firmware Update 28 | 0 | 0 | FW_UPDATE_28 | 20508 | 501C | 201 | - | unsigned | 0 | 65535 | 0
Firmware Update 29 | 0 | 0 | FW_UPDATE_29 | 20509 | 501D | 202 | - | unsigned | 0 | 65535 | 0
Firmware Update 30 | 0 | 0 | FW_UPDATE_30 | 20510 | 501E | 203 | - | unsigned | 0 | 65535 | 0
Firmware Update 31 | 0 | 0 | FW_UPDATE_31 | 20511 | 501F | 204 | - | unsigned | 0 | 65535 | 0
Firmware Update 32 | 0 | 0 | FW_UPDATE_32 | 20512 | 5020 | 205 | - | unsigned | 0 | 65535 | 0
Firmware Update 33 | 0 | 0 | FW_UPDATE_33 | 20513 | 5021 | 206 | - | unsigned | 0 | 65535 | 0
Firmware Update 34 | 0 | 0 | FW_UPDATE_34 | 20514 | 5022 | 207 | - | unsigned | 0 | 65535 | 0
Firmware Update 35 | 0 | 0 | FW_UPDATE_35 | 20515 | 5023 | 208 | - | unsigned | 0 | 65535 | 0
Firmware Update 36 | 0 | 0 | FW_UPDATE_36 | 20516 | 5024 | 209 | - | unsigned | 0 | 65535 | 0
Firmware Update 37 | 0 | 0 | FW_UPDATE_37 | 20517 | 5025 | 210 | - | unsigned | 0 | 65535 | 0
Firmware Update 38 | 0 | 0 | FW_UPDATE_38 | 20518 | 5026 | 211 | - | unsigned | 0 | 65535 | 0
Firmware Update 39 | 0 | 0 | FW_UPDATE_39 | 20519 | 5027 | 212 | - | unsigned | 0 | 65535 | 0
Firmware Update 40 | 0 | 0 | FW_UPDATE_40 | 20520 | 5028 | 213 | - | unsigned | 0 | 65535 | 0
Firmware Update 41 | 0 | 0 | FW_UPDATE_41 | 20521 | 5029 | 214 | - | unsigned | 0 | 65535 | 0
Firmware Update 42 | 0 | 0 | FW_UPDATE_42 | 20522 | 502A | 215 | - | unsigned | 0 | 65535 | 0
Firmware Update 43 | 0 | 0 | FW_UPDATE_43 | 20523 | 502B | 216 | - | unsigned | 0 | 65535 | 0
Firmware Update 44 | 0 | 0 | FW_UPDATE_44 | 20524 | 502C | 217 | - | unsigned | 0 | 65535 | 0
Firmware Update 45 | 0 | 0 | FW_UPDATE_45 | 20525 | 502D | 218 | - | unsigned | 0 | 65535 | 0
Firmware Update 46 | 0 | 0 | FW_UPDATE_46 | 20526 | 502E | 219 | - | unsigned | 0 | 65535 | 0
Firmware Update 47 | 0 | 0 | FW_UPDATE_47 | 20527 | 502F | 220 | - | unsigned | 0 | 65535 | 0
Firmware Update 48 | 0 | 0 | FW_UPDATE_48 | 20528 | 5030 | 221 | - | unsigned | 0 | 65535 | 0
Firmware Update 49 | 0 | 0 | FW_UPDATE_49 | 20529 | 5031 | 222 | - | unsigned | 0 | 65535 | 0
Firmware Update 50 | 0 | 0 | FW_UPDATE_50 | 20530 | 5032 | 223 | - | unsigned | 0 | 65535 | 0
Firmware Update 51 | 0 | 0 | FW_UPDATE_51 | 20531 | 5033 | 224 | - | unsigned | 0 | 65535 | 0
Firmware Update 52 | 0 | 0 | FW_UPDATE_52 | 20532 | 5034 | 225 | - | unsigned | 0 | 65535 | 0
Firmware Update 53 | 0 | 0 | FW_UPDATE_53 | 20533 | 5035 | 226 | - | unsigned | 0 | 65535 | 0
Firmware Update 54 | 0 | 0 | FW_UPDATE_54 | 20534 | 5036 | 227 | - | unsigned | 0 | 65535 | 0
Firmware Update 55 | 0 | 0 | FW_UPDATE_55 | 20535 | 5037 | 228 | - | unsigned | 0 | 65535 | 0
Firmware Update 56 | 0 | 0 | FW_UPDATE_56 | 20536 | 5038 | 229 | - | unsigned | 0 | 65535 | 0
Firmware Update 57 | 0 | 0 | FW_UPDATE_57 | 20537 | 5039 | 230 | - | unsigned | 0 | 65535 | 0
Firmware Update 58 | 0 | 0 | FW_UPDATE_58 | 20538 | 503A | 231 | - | unsigned | 0 | 65535 | 0
Firmware Update 59 | 0 | 0 | FW_UPDATE_59 | 20539 | 503B | 232 | - | unsigned | 0 | 65535 | 0
Firmware Update 60 | 0 | 0 | FW_UPDATE_60 | 20540 | 503C | 233 | - | unsigned | 0 | 65535 | 0
Firmware Update 61 | 0 | 0 | FW_UPDATE_61 | 20541 | 503D | 234 | - | unsigned | 0 | 65535 | 0
Firmware Update 62 | 0 | 0 | FW_UPDATE_62 | 20542 | 503E | 235 | - | unsigned | 0 | 65535 | 0
Firmware Update 63 | 0 | 0 | FW_UPDATE_63 | 20543 | 503F | 236 | - | unsigned | 0 | 65535 | 0
Firmware Update CRC Low Word | 0 | 0 | FW_UPDATE_CRC_LW | 20544 | 5040 | 237 | - | unsigned | 0 | 65535 | 0
Firmware Update CRC High Word | 0 | 0 | FW_UPDATE_CRC_HW | 20545 | 5041 | 238 | - | unsigned | 0 | 65535 | 0
Firmware Update State | 0 | 0 | FW_UPDATE_STATE | 20546 | 5042 | 239 | - | unsigned | 0 | 65535 | 0
Note on A72: Autor: HB: 0xAB as constant for eepromVersion detection LB: starting at 00..FF
Note on B72: Autor: eepromVersion must be the first element of all EEPROM variables
Note on A74: Autor: MODBUS ADDRESS: Read and Write a user-specific or random generated modbus address
Note on A75: Autor: TIMEOUT: Modbus timeout after which a request is canceled (no response received in this time)
Note on A76: Autor: HIGHBYTE = COMMAND LOWBYTE = DEVICE TYPE Command 1 = Generate new random address Device Type 0 = Execute command on all device types Device Type >0 = Execute command only on devices with the same device type
Note on A77: Autor: 0x4578 = Flash Area 0x210 - 0x2FF is unlocked
Note on A111: Autor: HB: Channel 0 LB: Channel 1
Note on A112: Autor: HB: Channel 2 LB: Channel 3
Note on A144: Autor: (0=normal, 1=only listen to IR and don't send, 2=Send a bad IR-signal after receiption)
Note on A151: Autor: (0=normal, 1=only listen to IR and don't send, 2=Send a bad IR-signal after receiption)
Note on D151: Autor: (0=normal, 1=only listen to IR and don't send, 2=Send a bad IR-signal after receiption)
Note on A154: Autor: Value in 20lx specified E.g. 2000lx = 100
Note on A156: Autor: Value in 20lx specified E.g. 2000lx = 100
Note on A159: Autor: Value in K steps 0…65535K
Note on A161: Autor: 0x0001 = FACTORY RESET 0x0002 = RESET 0x0008 = MANUFACTURER RESET 0x6400 = SELFTEST 0x6500 = SELFTEST END
Note on A163: Autor: LB: ID HB: >0 when master mode active
Note on A164: Autor: Specifies the choosen master in the area HB: Distanz to master LB: ID of master
Note on A165: Autor: Gives information about the actual active master HB: Master brightness LB: Local calculated brightness
Note on A166: Autor: Reduction of the brightness received from the master
Note on A168: Autor: LB: Counter HB: Distanz to master

## DiscreteInputs
#Name | Short-Name | MB-Adr (hex) | Index | Default
#Systemstatus
Zellspannung 1 ueberschreitet das obere Limit | C1OV | 1 | 0 | 0
Zellspannung 2 ueberschreitet das obere Limit | C2OV | 2 | 1 | 0
Zellspannung 3 ueberschreitet das obere Limit | C3OV | 3 | 2 | 0
Zellspannung 4 ueberschreitet das obere Limit | C4OV | 4 | 3 | 0
Zellspannung 5 ueberschreitet das obere Limit | C5OV | 5 | 4 | 0
Zellspannung 6 ueberschreitet das obere Limit | C6OV | 6 | 5 | 0
Zellspannung 7 ueberschreitet das obere Limit | C7OV | 7 | 6 | 0
Zellspannung 8 ueberschreitet das obere Limit | C8OV | 8 | 7 | 0
Zellspannung 9 ueberschreitet das obere Limit | C9OV | 9 | 8 | 0
Zellspannung 10 ueberschreitet das obere Limit | C10OV | 10 | 9 | 0
Zellspannung 11 ueberschreitet das obere Limit | C11OV | 11 | 10 | 0
Zellspannung 12 ueberschreitet das obere Limit | C12OV | 12 | 11 | 0
Zellspannung 13 ueberschreitet das obere Limit | C13OV | 13 | 12 | 0
Zellspannung 14 ueberschreitet das obere Limit | C14OV | 14 | 13 | 0
Zellspannung 15 ueberschreitet das obere Limit | C15OV | 15 | 14 | 0
Zellspannung 16 ueberschreitet das obere Limit | C16OV | 16 | 15 | 0
Zellspannung 17 ueberschreitet das obere Limit | C17OV | 17 | 16 | 0
Zellspannung 18 ueberschreitet das obere Limit | C18OV | 18 | 17 | 0
Zellspannung 19 ueberschreitet das obere Limit | C19OV | 19 | 18 | 0
Zellspannung 20 ueberschreitet das obere Limit | C20OV | 20 | 19 | 0
Zellspannung 21 ueberschreitet das obere Limit | C21OV | 21 | 20 | 0
Zellspannung 22 ueberschreitet das obere Limit | C22OV | 22 | 21 | 0
Zellspannung 23 ueberschreitet das obere Limit | C23OV | 23 | 22 | 0
Zellspannung 24 ueberschreitet das obere Limit | C24OV | 24 | 23 | 0
Zellspannung 1 unterschreitet das untere Limit | C1UV | 25 | 24 | 0
Zellspannung 2 unterschreitet das obere Limit | C2UV | 26 | 25 | 0
Zellspannung 3 unterschreitet das obere Limit | C3UV | 27 | 26 | 0
Zellspannung 4 unterschreitet das obere Limit | C4UV | 28 | 27 | 0
Zellspannung 5 unterschreitet das obere Limit | C5UV | 29 | 28 | 0
Zellspannung 6 unterschreitet das obere Limit | C6UV | 30 | 29 | 0
Zellspannung 7 unterschreitet das obere Limit | C7UV | 31 | 30 | 0
Zellspannung 8 unterschreitet das obere Limit | C8UV | 32 | 31 | 0
Zellspannung 9 unterschreitet das obere Limit | C9UV | 33 | 32 | 0
Zellspannung 10 unterschreitet das obere Limit | C10UV | 34 | 33 | 0
Zellspannung 11 unterschreitet das obere Limit | C11UV | 35 | 34 | 0
Zellspannung 12 unterschreitet das obere Limit | C12UV | 36 | 35 | 0
Zellspannung 13 unterschreitet das untere Limit | C13UV | 37 | 36 | 0
Zellspannung 14 unterschreitet das obere Limit | C14UV | 38 | 37 | 0
Zellspannung 15 unterschreitet das obere Limit | C15UV | 39 | 38 | 0
Zellspannung 16 unterschreitet das obere Limit | C16UV | 40 | 39 | 0
Zellspannung 17 unterschreitet das obere Limit | C17UV | 41 | 40 | 0
Zellspannung 18 unterschreitet das obere Limit | C18UV | 42 | 41 | 0
Zellspannung 19 unterschreitet das obere Limit | C19UV | 43 | 42 | 0
Zellspannung 20 unterschreitet das obere Limit | C20UV | 44 | 43 | 0
Zellspannung 21 unterschreitet das obere Limit | C21UV | 45 | 44 | 0
Zellspannung 22 unterschreitet das obere Limit | C22UV | 46 | 45 | 0
Zellspannung 23 unterschreitet das obere Limit | C23UV | 47 | 46 | 0
Zellspannung 24 unterschreitet das obere Limit | C24UV | 48 | 47 | 0
Die Gesamtbatteriespannung ueberschreitet das obere Limit | BATHIGH | 49 | 48 | 0
Die Gesamtbatteriespannung ueberschreitet das untere Limit | BATLOW | 50 | 49 | 0
Batterie wird aktuell entladen | DSG | 51 | 50 | 0
Die Batterie ist voll aufgeladen | FC | 52 | 51 | 0
Die Batteriekapazitaet unterschreitet die erste Warnschwelle | SOC1 | 53 | 52 | 0
Die Batteriekapazitaet unterschreitet die zweite finale Warnschwelle | SOCF | 54 | 53 | 0
Die Batterietemperatur ist ausserhalb des zulaessigen Bereichs fuer Ladung | CHG_INH | 55 | 54 | 0
uebertemperatur bei Laden | OTC | 56 | 55 | 0
(Schnell-)Laden erlaubt | CHG | 57 | 56 | 0
Internen Kurzschluss detektiert | ISD | 58 | 57 | 0
uebertemperatur bei Entladen | OTD | 59 | 58 | 0
#Geraetestatus
Error in bamo_modbus_vars | BAMO_MODBUS_VARS_ERR | 60 | 59 | 0
Error in modbus_slave_if | BAMO_MODBUS_SLAVE_IF_ERR | 61 | 60 | 0
Error in ltc6804_ctrl | BAMO_LTC6804_CTRL_ERR | 62 | 61 | 0
Error in bq34z110_ctrl | BAMO_BQ34Z110_CTRL_ERR | 63 | 62 | 0
Error in ntc_ctrl | BAMO_NTC_CTRL_ERR | 64 | 63 | 0
Error in modbus_serial | BAMO_MODBUS_SERIAL_ERR | 65 | 64 | 0
Error in ltc6804_spi | BAMO_LTC6804_SPI_ERR | 66 | 65 | 0
Error in bq34z110_i2c | BAMO_BQ34Z110_I2C_ERR | 67 | 66 | 0
Error in anain | BAMO_ANAIN_ERR | 68 | 67 | 0
Error in rst_ctrl | BAMO_RST_CTRL_ERR | 69 | 68 | 0

## Coils
#Name | Short-Name | MB-Adr (hex) | Index | Default
#
BaMo software reset | SW_RST | 0 | 0 | 0
Processor reset | PROC_RST | 1 | 1 | 0
BaMo system reset | SYS_RST | 2 | 2 | 0
BaMo factory reset | FCT_RST | 3 | 3 | 0
BaMo On/Off | ON_OFF | 4 | 4 | 1
#STOP