## Funktionen
BaMo MODBUS | Function | Sub-function | Supported | Note
Data access | Read Coils |  | Yes
| Read Discrete Inputs |  | Yes
| Read Holding Registers |  | Yes
| Read Input Register |  | Yes
| Write Single Coil |  | Yes
| Write Single Register |  | Yes
| Write Multiple Coils |  | Yes
| Write Multiple Registers |  | Yes
| Read/Write Multiple Registers |  | No
| Mask Write Register |  | No
| Read FIFO queue |  | No
Diagnostics | Read Exception Status |  | No
| Diagnostic | Return Query Data | Yes | loopback
|  | Restart Communications Option | No
|  | Return Diagnostic Register | No | diagnostic register to be defined
|  | Change ASCII Input Delimiter | No
|  | Force Listen Only Mode | Yes | no response to requests
|  | Clear Counters and Diagnostic Register | Yes
|  | Return Bus Message Count | Yes | Received frames total (Req, ack)
|  | Return Bus Communication Error Count | Yes | Received frames with CRC error
|  | Return Bus Exception Error Count | Yes | Anzahl exception responses von Slave
|  | Return Slave Message Count | Yes | Anzahl CRC-ok requests an slave incl. broadcasts.
|  | Return Slave No Response Count | Yes | Anzahl CRC-ok Req ohne response
|  | Return Slave NAK Count | Yes | Anzahl NAK exception responses
|  | Return Slave Busy Count | No
|  | Return Bus Character Overrun Count | No
|  | Clear Overrun Counter and Flag | No
| Get Com event counter |  | No | Status (idle, busy), com event counter
| Get Com Event Log |  | No | Status, com event counter, bus message count, 0..64 event bytes ( Receive Event, Send Event, Entered Listen Only Mode,Initiated Communication Restart
| Report Slave ID |  | No | slave ID, status, additional data
| Read device Identification |  | No
File record access | Read File record |  | No
| Write File record |  | No
Other | Encapsulated Interface Transport |  | No

## Master
#Modbus Slave Nodes
#Bezeichnung der Modbus Slave Nodes
Panel
Panel
Sensormodule
Sensormodule
Sensormodule
Sensormodule
AloneATWork
pcbridge
clm

## Slave
#Modbus Slave
#Generelle Informationen
mySlaveDeviceType=2
mySlaveDeviceAddress=8

## InputRegister
#Name | Short-Name | MB-Adr (hex) | Index | Einheit | Type | Default
#Ladezustand
Spezifizierte Batteriekapazitaet | DESIGN_CAPACITY | 1 | 0 | 10 mAh | unsigned | 0
Berechnete kompensierte Gesamtbatteriekapazitaet | FULL_CHARGE_CAPACITY | 2 | 1 | 10 mAh | unsigned | 0
Unkompensierte Gesamtkapazitaet | FULL_AVAILABLE_CAPACITY | 3 | 2 | 10 mAh | unsigned | 0
Momentaner Ladezustand in % von der berechneten Gesamtkapazitaet | STATE_OF_CHARGE | 4 | 3 | % | unsigned | 0
Momentan verfuegbare kompensierte Batteriekapazitaet | REMAINING_CAPACITY | 5 | 4 | 10 mAh | unsigned | 0
Momentan verfuegbare unkompensierte Batteriekapazitaet | NOMINAL_AVAILABLE_CAPACITY | 6 | 5 | 10 mAh | unsigned | 0
Momentan verfuegbare Restenergie | AVAILABLE_ENERGY | 7 | 6 | Wh | unsigned | 0
Momentan verfuegbare Restleistung | AVAILABLE_POWER | 8 | 7 | W | unsigned | 0
Restlaufzeit bei bestimmtem Entladestrom | ATRATE_TIME_TO_EMPTY | 9 | 8 | min | unsigned | 0
Restlaufzeit bei momentanem Entladestrom | TIME_TO_EMPTY | 10 | 9 | min | unsigned | 0
Restlaufzeit bei maximalem Entladestrom | MAX_LOAD_TIME_TO_EMPTY | 11 | 10 | min | unsigned | 0
Restlaufzeit bei Standby-Entladestrom | STANDBY_TIME_TO_EMPTY | 12 | 11 | min | unsigned | 0
Restlaufzeit bei durchschnittlicher Entladeleistung | TIME_TO_EMPTY_AT_CONSTANT_POWER | 13 | 12 | min | unsigned | 0
Restladezeit bei durchschnittlichem Entladestrom | TIME_TO_FULL | 14 | 13 | min | unsigned | 0
Spezifizierte Batteriekapazitaet vs. Berechnete Gesamtbatteriekapazitaet | STATE_OF_HEALTH | 15 | 14 | % | unsigned | 0
Statusinformationen vom TI BQ34Z110 | CONTROL_STATUS | 16 | 15 | # | unsigned | 0
#Spannung
Aktuelle Gesamtbatteriespannung | VOLTAGE | 17 | 16 | mV | unsigned | 0
Spannung Zelle 1 | VOLTAGE_CELL_1 | 18 | 17 | 0.1 mV | unsigned | 0
Spannung Zelle 2 | VOLTAGE_CELL_2 | 19 | 18 | 0.1 mV | unsigned | 0
Spannung Zelle 3 | VOLTAGE_CELL_3 | 20 | 19 | 0.1 mV | unsigned | 0
Spannung Zelle 4 | VOLTAGE_CELL_4 | 21 | 20 | 0.1 mV | unsigned | 0
Spannung Zelle 5 | VOLTAGE_CELL_5 | 22 | 21 | 0.1 mV | unsigned | 0
Spannung Zelle 6 | VOLTAGE_CELL_6 | 23 | 22 | 0.1 mV | unsigned | 0
Spannung Zelle 7 | VOLTAGE_CELL_7 | 24 | 23 | 0.1 mV | unsigned | 0
Spannung Zelle 8 | VOLTAGE_CELL_8 | 25 | 24 | 0.1 mV | unsigned | 0
Spannung Zelle 9 | VOLTAGE_CELL_9 | 26 | 25 | 0.1 mV | unsigned | 0
Spannung Zelle 10 | VOLTAGE_CELL_10 | 27 | 26 | 0.1 mV | unsigned | 0
Spannung Zelle 11 | VOLTAGE_CELL_11 | 28 | 27 | 0.1 mV | unsigned | 0
Spannung Zelle 12 | VOLTAGE_CELL_12 | 29 | 28 | 0.1 mV | unsigned | 0
Spannung Zelle 13 | VOLTAGE_CELL_13 | 30 | 29 | 0.1 mV | unsigned | 0
Spannung Zelle 14 | VOLTAGE_CELL_14 | 31 | 30 | 0.1 mV | unsigned | 0
Spannung Zelle 15 | VOLTAGE_CELL_15 | 32 | 31 | 0.1 mV | unsigned | 0
Spannung Zelle 16 | VOLTAGE_CELL_16 | 33 | 32 | 0.1 mV | unsigned | 0
Spannung Zelle 17 | VOLTAGE_CELL_17 | 34 | 33 | 0.1 mV | unsigned | 0
Spannung Zelle 18 | VOLTAGE_CELL_18 | 35 | 34 | 0.1 mV | unsigned | 0
Spannung Zelle 19 | VOLTAGE_CELL_19 | 36 | 35 | 0.1 mV | unsigned | 0
Spannung Zelle 20 | VOLTAGE_CELL_20 | 37 | 36 | 0.1 mV | unsigned | 0
Spannung Zelle 21 | VOLTAGE_CELL_21 | 38 | 37 | 0.1 mV | unsigned | 0
Spannung Zelle 22 | VOLTAGE_CELL_22 | 39 | 38 | 0.1 mV | unsigned | 0
Spannung Zelle 23 | VOLTAGE_CELL_23 | 40 | 39 | 0.1 mV | unsigned | 0
Spannung Zelle 24 | VOLTAGE_CELL_24 | 41 | 40 | 0.1 mV | unsigned | 0
Empfohlene Ladespannung [mV] | CHARGE_VOLTAGE | 42 | 41 | mV | unsigned | 0
#Strom
Durchschnittlicher Lade- bzw. Entladestrom | AVERAGE_CURRENT | 43 | 42 | 10 mA | signed | 0
Momentaner Lade- bzw. Entladestrom | CURRENT | 44 | 43 | 10 mA | signed | 0
Maximaler Entladestrom im aktuellen Ladezyklus | MAX_LOAD_CURRENT | 45 | 44 | 10 mA | signed | 0
Standby Strom | STANDBY_CURRENT | 46 | 45 | 10 mA | signed | 0
Durchschnittliche Entladeleistung | AVERAGE_POWER | 47 | 46 | W | unsigned | 0
Empfohlener Ladestrom | CHARGE_CURRENT | 48 | 47 | 10 mA | signed | 0
Schaetzung des Selbstentladestroms | SELF_DISCHARGE_CURRENT | 49 | 48 | 10 mA | signed | 0
Anzahl Entladezyklen | CYCLE_COUNT | 50 | 49 | # | unsigned | 0
#Temperatur
Temperaturmesswert NTC 1 (PC 0) | NTC_PC_0 | 51 | 50 | 0.01°C | signed | 0
Temperaturmesswert NTC 2 (PC 1) | NTC_PC_1 | 52 | 51 | 0.01°C | signed | 0
Temperaturmesswert NTC 3 (LTC 0) | NTC_LTC_0 | 53 | 52 | 0.01°C | signed | 0
Temperaturmesswert NTC 4 (LTC 1) | NTC_LTC_1 | 54 | 53 | 0.01°C | signed | 0
Temperaturmesswert NTC 5 (LTC 2) | NTC_LTC_2 | 55 | 54 | 0.01°C | signed | 0
Temperaturmesswert NTC 6 (BQZ) | NTC_BQZ | 56 | 55 | 0.01°C | signed | 0
#LTC6804
Gesamtspannung | LTC6804_SOC_1 | 57 | 56 | mV | unsigned | 0
Gesamtspannung | LTC6804_SOC_2 | 58 | 57 | mV | unsigned | 0
Analogspannung | LTC6804_VA_1 | 59 | 58 | 0.1 mV | unsigned | 0
Analogspannung | LTC6804_VA_2 | 60 | 59 | 0.1 mV | unsigned | 0
Digitalspannung | LTC6804_VD_1 | 61 | 60 | 0.1 mV | unsigned | 0
Digitalspannung | LTC6804_VD_2 | 62 | 61 | 0.1 mV | unsigned | 0
Referenzspannung U_ref2 | LTC6804_REF2_1 | 63 | 62 | 0.1 mV | unsigned | 0
Referenzspannung U_ref2 | LTC6804_REF2_2 | 64 | 63 | 0.1 mV | unsigned | 0
#DEVICE information
Manufacturer | DEV_MANUFACTURER | 65 | 64 | ASCII | unsigned | 83
Manufacturer 1 | DEV_MANUFACTURER_1 | 66 | 65 | ASCII | unsigned | 97
Manufacturer 2 | DEV_MANUFACTURER_2 | 67 | 66 | ASCII | unsigned | 117
Manufacturer 3 | DEV_MANUFACTURER_3 | 68 | 67 | ASCII | unsigned | 116
Manufacturer 4 | DEV_MANUFACTURER_4 | 69 | 68 | ASCII | unsigned | 101
Manufacturer 5 | DEV_MANUFACTURER_5 | 70 | 69 | ASCII | unsigned | 114
Manufacturer 6 | DEV_MANUFACTURER_6 | 71 | 70 | ASCII | unsigned | 32
Manufacturer 7 | DEV_MANUFACTURER_7 | 72 | 71 | ASCII | unsigned | 76
Manufacturer 8 | DEV_MANUFACTURER_8 | 73 | 72 | ASCII | unsigned | 116
Manufacturer 9 | DEV_MANUFACTURER_9 | 74 | 73 | ASCII | unsigned | 100
Manufacturer 10 | DEV_MANUFACTURER_10 | 75 | 74 | ASCII | unsigned | 0
Device Name | DEV_NAME | 76 | 75 | ASCII | unsigned | 66
Device Name 1 | DEV_NAME_1 | 77 | 76 | ASCII | unsigned | 97
Device Name 2 | DEV_NAME_2 | 78 | 77 | ASCII | unsigned | 77
Device Name 3 | DEV_NAME_3 | 79 | 78 | ASCII | unsigned | 111
Device Name 4 | DEV_NAME_4 | 80 | 79 | ASCII | unsigned | 0
Device Type | DEV_TYPE | 81 | 80 | # | unsigned | 1
Release Version | VERSION_RELEASE | 82 | 81 | # | unsigned | 1
Major Version | VERSION_MAJOR | 83 | 82 | # | unsigned | 0
Minor Version | VERSION_MINOR | 84 | 83 | # | unsigned | 1
Build | BUILD | 85 | 84 | ASCII | unsigned | 0
Build 1 | BUILD_1 | 86 | 85 | ASCII | unsigned | 0
Build 2 | BUILD_2 | 87 | 86 | ASCII | unsigned | 0
Build 3 | BUILD_3 | 88 | 87 | ASCII | unsigned | 0
Build 4 | BUILD_4 | 89 | 88 | ASCII | unsigned | 0
Build 5 | BUILD_5 | 90 | 89 | ASCII | unsigned | 0
Build 6 | BUILD_6 | 91 | 90 | ASCII | unsigned | 0
Build 7 | BUILD_7 | 92 | 91 | ASCII | unsigned | 0
Build 8 | BUILD_8 | 93 | 92 | ASCII | unsigned | 0
Build 9 | BUILD_9 | 94 | 93 | ASCII | unsigned | 0

## HoldingRegister
#Name | EEPROM | Master-Mirror | Short-Name | MB-Adr (dezimal) | MB-Adr (hex) | Index | Einheit | Type | Min | Max | Default
#Konfiguration
firmwareProject 'oc' control_unit_lightpad | 0 | 0 | FW_VERSION | 0 | 0 | 0 | char | unsigned | 0 | 65535 | 0
firmwareProject 'tn' | 0 | 0 | FW_VERSION_1 | 1 | 1 | 1 | char | unsigned | 0 | 65535 | 0
firmwareProject 'or' | 0 | 0 | FW_VERSION_2 | 2 | 2 | 2 | char | unsigned | 0 | 65535 | 0
firmwareProject '_l' | 0 | 0 | FW_VERSION_3 | 3 | 3 | 3 | char | unsigned | 0 | 65535 | 0
firmwareProject 'om' | 0 | 0 | FW_VERSION_4 | 4 | 4 | 4 | char | unsigned | 0 | 65535 | 0
firmwareProject 'ud' | 0 | 0 | FW_VERSION_5 | 5 | 5 | 5 | char | unsigned | 0 | 65535 | 0
firmwareProject '_l'sfasdafdsfdsf | 0 | 0 | FW_VERSION_6 | 6 | 6 | 6 | char | unsigned | 0 | 65535 | 0
firmwareProject 'il' | 0 | 0 | FW_VERSION_7 | 7 | 7 | 7 | char | unsigned | 0 | 65535 | 0
firmwareProject 'hg' | 0 | 0 | FW_VERSION_8 | 8 | 8 | 8 | char | unsigned | 0 | 65535 | 0
firmwareProject 'pt' | 0 | 0 | FW_VERSION_9 | 9 | 9 | 9 | char | unsigned | 0 | 65535 | 0
firmwareProject 'da' | 0 | 0 | FW_VERSION_10 | 10 | A | 10 | char | unsigned | 0 | 65535 | 0
firmwareVersion [0] ['-'] - 01.00 | 0 | 0 | FW_VERSION_11 | 11 | B | 11 | char | unsigned | 0 | 65535 | 0
firmwareVersion ['.'] [1] | 0 | 0 | FW_VERSION_12 | 12 | C | 12 | char | unsigned | 0 | 65535 | 0
firmwareVersion [3] [2] | 0 | 0 | FW_VERSION_13 | 13 | D | 13 | char | unsigned | 0 | 65535 | 0
firmwareBuild [0] ['.'] .01 | 0 | 0 | FW_VERSION_14 | 14 | E | 14 | char | unsigned | 0 | 65535 | 0
firmwareBuild ['-'] [1] | 0 | 0 | FW_VERSION_15 | 15 | F | 15 | char | unsigned | 0 | 65535 | 0
gitCommit [1] [0] 8 characters | 0 | 0 | FW_VERSION_16 | 16 | 10 | 16 | - | unsigned | 0 | 65535 | 0
gitCommit [3] [2] | 0 | 0 | FW_VERSION_17 | 17 | 11 | 17 | - | unsigned | 0 | 65535 | 0
gitCommit [5] [4] | 0 | 0 | FW_VERSION_18 | 18 | 12 | 18 | - | unsigned | 0 | 65535 | 0
gitCommit [7] [6] | 0 | 0 | FW_VERSION_19 | 19 | 13 | 19 | - | unsigned | 0 | 65535 | 0
firmwareTarget [r] ['-'] rel | 0 | 0 | FW_VERSION_20 | 20 | 14 | 20 | - | unsigned | 0 | 65535 | 0
firmwareTarget [l] [e] | 0 | 0 | FW_VERSION_21 | 21 | 15 | 21 | - | unsigned | 0 | 65535 | 0
not used | 0 | 0 | FW_VERSION_22 | 22 | 16 | 22 | - | unsigned | 0 | 65535 | 0
not used | 0 | 0 | FW_VERSION_23 | 23 | 17 | 23 | - | unsigned | 0 | 65535 | 0
not used | 0 | 0 | FW_VERSION_24 | 24 | 18 | 24 | - | unsigned | 0 | 65535 | 0
not used | 0 | 0 | FW_VERSION_25 | 25 | 19 | 25 | - | unsigned | 0 | 65535 | 0
not used | 0 | 0 | FW_VERSION_26 | 26 | 1A | 26 | - | unsigned | 0 | 65535 | 0
not used | 0 | 0 | FW_VERSION_27 | 27 | 1B | 27 | - | unsigned | 0 | 65535 | 0
not used | 0 | 0 | FW_VERSION_28 | 28 | 1C | 28 | - | unsigned | 0 | 65535 | 0
not used | 0 | 0 | FW_VERSION_29 | 29 | 1D | 29 | - | unsigned | 0 | 65535 | 0
not used | 0 | 0 | FW_VERSION_30 | 30 | 1E | 30 | - | unsigned | 0 | 65535 | 0
not used | 0 | 0 | FW_VERSION_31 | 31 | 1F | 31 | - | unsigned | 0 | 65535 | 0
hwVersions '61' 1601-2 | 0 | 0 | HW_VERSION | 48 | 30 | 32 | char | unsigned | 0 | 65535 | 0
hwVersions '10' | 0 | 0 | HW_VERSION_1 | 49 | 31 | 33 | char | unsigned | 0 | 65535 | 0
hwVersions '2-' | 0 | 0 | HW_VERSION_2 | 50 | 32 | 34 | char | unsigned | 0 | 65535 | 0
hwVersions '0v' | 0 | 0 | HW_VERSION_3 | 51 | 33 | 35 | char | unsigned | 0 | 65535 | 0
hwVersions '0v' | 0 | 0 | HW_VERSION_4 | 52 | 34 | 36 | char | unsigned | 0 | 65535 | 0
firmwareProject 'ob' bootloader_control_unit_M3 | 0 | 0 | FW_VERSION_BL | 53 | 35 | 37 | char | unsigned | 0 | 65535 | 0
firmwareProject 'to' | 0 | 0 | FW_VERSION_BL_1 | 54 | 36 | 38 | char | unsigned | 0 | 65535 | 0
firmwareProject 'ol' | 0 | 0 | FW_VERSION_BL_2 | 55 | 37 | 39 | char | unsigned | 0 | 65535 | 0
firmwareProject 'da' | 0 | 0 | FW_VERSION_BL_3 | 56 | 38 | 40 | char | unsigned | 0 | 65535 | 0
firmwareProject 're' | 0 | 0 | FW_VERSION_BL_4 | 57 | 39 | 41 | char | unsigned | 0 | 65535 | 0
firmwareProject 'c_' | 0 | 0 | FW_VERSION_BL_5 | 58 | 3A | 42 | char | unsigned | 0 | 65535 | 0
firmwareProject 'no' | 0 | 0 | FW_VERSION_BL_6 | 59 | 3B | 43 | char | unsigned | 0 | 65535 | 0
firmwareProject 'rt' | 0 | 0 | FW_VERSION_BL_7 | 60 | 3C | 44 | char | unsigned | 0 | 65535 | 0
firmwareProject 'lo' | 0 | 0 | FW_VERSION_BL_8 | 61 | 3D | 45 | char | unsigned | 0 | 65535 | 0
firmwareProject 'u_' | 0 | 0 | FW_VERSION_BL_9 | 62 | 3E | 46 | char | unsigned | 0 | 65535 | 0
firmwareProject 'in' | 0 | 0 | FW_VERSION_BL_10 | 63 | 3F | 47 | char | unsigned | 0 | 65535 | 0
firmwareProject '_t' | 0 | 0 | FW_VERSION_BL_11 | 64 | 40 | 48 | char | unsigned | 0 | 65535 | 0
firmwareProject 'M3' | 0 | 0 | FW_VERSION_BL_12 | 65 | 41 | 49 | char | unsigned | 0 | 65535 | 0
firmwareVersion [0] ['-'] - 01.00 | 0 | 0 | FW_VERSION_BL_13 | 66 | 42 | 50 | char | unsigned | 0 | 65535 | 0
firmwareVersion ['.'] [1] | 0 | 0 | FW_VERSION_BL_14 | 67 | 43 | 51 | char | unsigned | 0 | 65535 | 0
firmwareVersion [3] [2] | 0 | 0 | FW_VERSION_BL_15 | 68 | 44 | 52 | char | unsigned | 0 | 65535 | 0
firmwareBuild [0] ['.'] .01 | 0 | 0 | FW_VERSION_BL_16 | 69 | 45 | 53 | - | unsigned | 0 | 65535 | 0
firmwareBuild ['-'] [1] | 0 | 0 | FW_VERSION_BL_17 | 70 | 46 | 54 | - | unsigned | 0 | 65535 | 0
gitCommit [1] [0] 8 characters | 0 | 0 | FW_VERSION_BL_18 | 71 | 47 | 55 | - | unsigned | 0 | 65535 | 0
gitCommit [3] [2] | 0 | 0 | FW_VERSION_BL_19 | 72 | 48 | 56 | - | unsigned | 0 | 65535 | 0
gitCommit [5] [4] | 0 | 0 | FW_VERSION_BL_20 | 73 | 49 | 57 | - | unsigned | 0 | 65535 | 0
gitCommit [7] [6] | 0 | 0 | FW_VERSION_BL_21 | 74 | 4A | 58 | - | unsigned | 0 | 65535 | 0
firmwareTarget [r] ['-'] rel | 0 | 0 | FW_VERSION_BL_22 | 75 | 4B | 59 | - | unsigned | 0 | 65535 | 0
firmwareTarget [l] [e] | 0 | 0 | FW_VERSION_BL_23 | 76 | 4C | 60 | - | unsigned | 0 | 65535 | 0
not used | 0 | 0 | FW_VERSION_BL_24 | 77 | 4D | 61 | - | unsigned | 0 | 65535 | 0
not used | 0 | 0 | FW_VERSION_BL_25 | 78 | 4E | 62 | - | unsigned | 0 | 65535 | 0
not used | 0 | 0 | FW_VERSION_BL_26 | 79 | 4F | 63 | - | unsigned | 0 | 65535 | 0
not used | 0 | 0 | FW_VERSION_BL_27 | 80 | 50 | 64 | - | unsigned | 0 | 65535 | 0
not used | 0 | 0 | FW_VERSION_BL_28 | 81 | 51 | 65 | - | unsigned | 0 | 65535 | 0
not used | 0 | 0 | FW_VERSION_BL_29 | 82 | 52 | 66 | - | unsigned | 0 | 65535 | 0
not used | 0 | 0 | FW_VERSION_BL_30 | 83 | 53 | 67 | - | unsigned | 0 | 65535 | 0
not used | 0 | 0 | FW_VERSION_BL_31 | 84 | 54 | 68 | - | unsigned | 0 | 65535 | 0
EEPROM Version | 1 | 0 | EEPROM_VERSION | 255 | FF | 69 | - | unsigned | 0 | 65535 | 43778
Device Type | 0 | 0 | DEVICE_TYPE | 256 | 100 | 70 | - | unsigned | 0 | 65535 | 2
(Random/Set) Modbus Address | 1 | 0 | MODBUS_ADDRESS | 257 | 101 | 71 | - | unsigned | 0 | 65535 | 8
Modbus Timeout + multiplikation Faktor Ligt Measuring | 1 | 0 | MODBUS_TIMEOUT_LIGHTMEASURING_MULTI_FAKTOR | 258 | 102 | 72 | - | unsigned | 0 | 65535 | 1556
Command - Devicetype | 0 | 0 | MODBUS_COMMAND | 259 | 103 | 73 | - | unsigned | 0 | 65535 | 0
Write SN/BIL/DATE/Order Code = BEEF - Erase // FLASH = DEAD | 0 | 0 | WRITE_MANUFACTURE_INFO | 512 | 200 | 74 | - | unsigned | 0 | 65535 | 0
serialNumber | 0 | 0 | SERIAL_NUMBER | 528 | 210 | 75 | char | unsigned | 0 | 65535 | 0
serialNumber | 0 | 0 | SERIAL_NUMBER_1 | 529 | 211 | 76 | char | unsigned | 0 | 65535 | 0
serialNumber | 0 | 0 | SERIAL_NUMBER_2 | 530 | 212 | 77 | char | unsigned | 0 | 65535 | 0
serialNumber | 0 | 0 | SERIAL_NUMBER_3 | 531 | 213 | 78 | char | unsigned | 0 | 65535 | 0
serialNumber | 0 | 0 | SERIAL_NUMBER_4 | 532 | 214 | 79 | char | unsigned | 0 | 65535 | 0
serialNumber | 0 | 0 | SERIAL_NUMBER_5 | 533 | 215 | 80 | char | unsigned | 0 | 65535 | 0
serialNumber | 0 | 0 | SERIAL_NUMBER_6 | 534 | 216 | 81 | char | unsigned | 0 | 65535 | 0
serialNumber | 0 | 0 | SERIAL_NUMBER_7 | 535 | 217 | 82 | char | unsigned | 0 | 65535 | 0
HW/BOM | 0 | 0 | HW_BOM_VERSION | 536 | 218 | 83 | char | unsigned | 0 | 65535 | 0
HW/BOM | 0 | 0 | HW_BOM_VERSION_1 | 537 | 219 | 84 | char | unsigned | 0 | 65535 | 0
HW/BOM | 0 | 0 | HW_BOM_VERSION_2 | 538 | 21A | 85 | char | unsigned | 0 | 65535 | 0
HW/BOM | 0 | 0 | HW_BOM_VERSION_3 | 539 | 21B | 86 | char | unsigned | 0 | 65535 | 0
HW/BOM | 0 | 0 | HW_BOM_VERSION_4 | 540 | 21C | 87 | char | unsigned | 0 | 65535 | 0
HW/BOM | 0 | 0 | HW_BOM_VERSION_5 | 541 | 21D | 88 | char | unsigned | 0 | 65535 | 0
HW/BOM | 0 | 0 | HW_BOM_VERSION_6 | 542 | 21E | 89 | char | unsigned | 0 | 65535 | 0
HW/BOM | 0 | 0 | HW_BOM_VERSION_7 | 543 | 21F | 90 | char | unsigned | 0 | 65535 | 0
Date | 0 | 0 | DATE | 544 | 220 | 91 | char | unsigned | 0 | 65535 | 0
Date | 0 | 0 | DATE_1 | 545 | 221 | 92 | char | unsigned | 0 | 65535 | 0
Date | 0 | 0 | DATE_2 | 546 | 222 | 93 | char | unsigned | 0 | 65535 | 0
Date | 0 | 0 | DATE_3 | 547 | 223 | 94 | char | unsigned | 0 | 65535 | 0
Date | 0 | 0 | DATE_4 | 548 | 224 | 95 | char | unsigned | 0 | 65535 | 0
Date | 0 | 0 | DATE_5 | 549 | 225 | 96 | char | unsigned | 0 | 65535 | 0
Date | 0 | 0 | DATE_6 | 550 | 226 | 97 | char | unsigned | 0 | 65535 | 0
Date | 0 | 0 | DATE_7 | 551 | 227 | 98 | char | unsigned | 0 | 65535 | 0
Regent Order Code | 0 | 0 | REGENT_ITEM_NUMBER | 552 | 228 | 99 | char | unsigned | 0 | 65535 | 0
Regent Order Code | 0 | 0 | REGENT_ITEM_NUMBER_1 | 553 | 229 | 100 | char | unsigned | 0 | 65535 | 0
Regent Order Code | 0 | 0 | REGENT_ITEM_NUMBER_2 | 554 | 22A | 101 | char | unsigned | 0 | 65535 | 0
Regent Order Code | 0 | 0 | REGENT_ITEM_NUMBER_3 | 555 | 22B | 102 | char | unsigned | 0 | 65535 | 0
Regent Order Code | 0 | 0 | REGENT_ITEM_NUMBER_4 | 556 | 22C | 103 | char | unsigned | 0 | 65535 | 0
Regent Order Code | 0 | 0 | REGENT_ITEM_NUMBER_5 | 557 | 22D | 104 | char | unsigned | 0 | 65535 | 0
Regent Order Code | 0 | 0 | REGENT_ITEM_NUMBER_6 | 558 | 22E | 105 | char | unsigned | 0 | 65535 | 0
Regent Order Code | 0 | 0 | REGENT_ITEM_NUMBER_7 | 559 | 22F | 106 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER | 560 | 230 | 107 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER_1 | 561 | 231 | 108 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER_2 | 562 | 232 | 109 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER_3 | 563 | 233 | 110 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER_4 | 564 | 234 | 111 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER_5 | 565 | 235 | 112 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER_6 | 566 | 236 | 113 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER_7 | 567 | 237 | 114 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER_8 | 568 | 238 | 115 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER_9 | 569 | 239 | 116 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER_10 | 570 | 23A | 117 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER_11 | 571 | 23B | 118 | char | unsigned | 0 | 65535 | 0
ModBus to DALI Gateway Response Channel 1 | 0 | 0 | MB2DALI_RESPONSE_CH1 | 4096 | 1000 | 119 | - | unsigned | 0 | 65535 | 0
ModBus to DALI Gateway Request Channel 1 | 0 | 0 | MB2DALI_REQUEST_CH1 | 4097 | 1001 | 120 | - | unsigned | 0 | 65535 | 0
ModBus to DALI Gateway Response Channel 2 | 0 | 0 | MB2DALI_RESPONSE_CH2 | 4098 | 1002 | 121 | - | unsigned | 0 | 65535 | 0
ModBus to DALI Gateway Request Channel 2 | 0 | 0 | MB2DALI_REQUEST_CH2 | 4099 | 1003 | 122 | - | unsigned | 0 | 65535 | 0
Number of Light Decks | 1 | 0 | NUMBER_OF_LIGHT_DECKS | 8193 | 2001 | 123 | - | unsigned | 0 | 5 | 5
Number of Panels | 1 | 0 | NUMBER_OF_PANELS | 8194 | 2002 | 124 | - | unsigned | 0 | 3 | 3
Nachlaufzeit Sensor | 1 | 0 | PIR_DELAY_TIME | 8195 | 2003 | 125 | [s] | unsigned | 0 | 65535 | 600
Security Light Level Nachlaufzeit | 1 | 0 | SECURITY_LIGHT_LEVEL_DELAY_TIME | 8196 | 2004 | 126 | [s] | unsigned | 0 | 65535 | 0
Einschwingzeit PIR | 1 | 0 | PIR_SETTING_TIME | 8197 | 2005 | 127 | [s] | unsigned | 0 | 30 | 10000
Features Sensormodule 1 Enable/Disable 1 = Enable 0 = Disable bitweise: [0]=pir [1]=ligtcontrol [2]=button | 1 | 0 | SENSORMODULE_MODE | 8198 | 2006 | 128 | - | unsigned | 0 | 65535 | 7
Features Sensormodule 2 Enable/Disable 1 = Enable 0 = Disable bitweise: [0]=pir [1]=ligtcontrol [2]=button | 1 | 0 | SENSORMODULE_MODE_1 | 8199 | 2007 | 129 | - | unsigned | 0 | 65535 | 7
Features Sensormodule 3 Enable/Disable 1 = Enable 0 = Disable bitweise: [0]=pir [1]=ligtcontrol [2]=button | 1 | 0 | SENSORMODULE_MODE_2 | 8200 | 2008 | 130 | - | unsigned | 0 | 65535 | 7
Features Sensormodule 4 Enable/Disable 1 = Enable 0 = Disable bitweise: [0]=pir [1]=ligtcontrol [2]=button | 1 | 0 | SENSORMODULE_MODE_3 | 8201 | 2009 | 131 | - | unsigned | 0 | 65535 | 7
Buttons Bedienelement 1 Enable / Disable 1 = Enable 0 = Disable bitweise: [0] = button 1 - [1] = button 2 - [2] = button 3 - [3] = led Bedienelement | 1 | 0 | PANEL_1_MODE | 8202 | 200A | 132 | - | unsigned | 0 | 65535 | 15
Buttons Bedienelement 2 Enable / Disable 1 = Enable 0 = Disable bitweise: [0] = button 1 - [1] = button 2 - [2] = button 3 - [3] = led Bedienelement | 1 | 0 | PANEL_2_MODE | 8203 | 200B | 133 | - | unsigned | 0 | 65535 | 15
Halbautomatic | 1 | 0 | HALF_AUTOMATIC_FLAG | 8204 | 200C | 134 | - | unsigned | 0 | 1 | 0
Sensodim Zuordnung 0 = Regelung auf jeweiligen Sensor - 1 = mittelwert aller Sensoren - 2 = Höchster Wert aller Sensoren - 3 = tiefster Wert aller Sensoren | 1 | 0 | SENSODIM_ASSIGNMENT | 8205 | 200D | 135 | - | unsigned | 0 | 3 | 0
Sollwert überschreibbar | 1 | 0 | ENABLE_OVERWRITE_SET_POINT | 8206 | 200E | 136 | - | unsigned | 0 | 1 | 1
min. safe point | 1 | 0 | MAX_SET_POINT_SENSOR | 8207 | 200F | 137 | lux | unsigned | 0 | 65535 | 5000
Fade Time Slow Dimming | 1 | 0 | FADE_TIME_SLOW_DIMMING | 8208 | 2010 | 138 | ms | unsigned | 0 | 65535 | 5000
Fade In Time | 1 | 0 | FADE_IN_TIME | 8209 | 2011 | 139 | ms | unsigned | 0 | 65535 | 2000
Fade Out Time | 1 | 0 | FADE_OUT_TIME | 8210 | 2012 | 140 | ms | unsigned | 0 | 65535 | 10000
Fade On Off Time | 1 | 0 | FADE_ON_OFF_TIME | 8211 | 2013 | 141 | ms | unsigned | 0 | 65535 | 500
Lightregulation Speed HB - 2-10 2 = sehr schnell - 10 = sehr langsam LB - hysteresis - default 5% | 1 | 0 | LIGHT_REGULATION_SPEED_HYSTERESIS | 8212 | 2014 | 142 | - | unsigned | 0 | 10 | 2053
Min Light Value | 1 | 0 | MIN_LIGHT_VALUE | 8213 | 2015 | 143 | DALI | unsigned | 104 | 144 | 104
Max Light Value | 1 | 0 | MAX_LIGHT_VALUE | 8214 | 2016 | 144 | DALI | unsigned | 104 | 144 | 254
hold override = einschalten mit dem letzten wert | 1 | 0 | HOLD_OVERRIDE_FLAG | 8215 | 2017 | 145 | - | unsigned | 0 | 1 | 1
Power Safe Mode | 1 | 0 | POWER_SAFE_MODE | 8216 | 2018 | 146 | - | unsigned | 0 | 1 | 1
Power Safe Treshold | 1 | 0 | POWER_SAFE_TRESHOLD | 8217 | 2019 | 147 | % | unsigned | 100 | 254 | 150
Power Safe Treshold Duration - nach wie langer Zeit überlicht geht man dann in den Brightout mode | 1 | 0 | POWER_SAFE_TRESHOLD_DURATION | 8218 | 201A | 148 | s | unsigned | 0 | 65535 | 600
Step UP DALI Value | 1 | 0 | DIM_STEP_UP | 8219 | 201B | 149 | DALI | unsigned | 1 | 100 | 10
Step DOWN DALI VALUE | 1 | 0 | DIM_STEP_DOWN | 8220 | 201C | 150 | DALI | unsigned | 1 | 100 | 10
Security Light Level | 1 | 0 | SECURITY_LIGHT_LEVEL | 8221 | 201D | 151 | DALI | unsigned | 0 | 254 | 0
Power UP bei Nezt ein - bitweise: [0]=head 1 [1]=head 2 etc. | 1 | 0 | POWER_UP_MODE | 8222 | 201E | 152 | - | unsigned | 0 | 1 | 0
Licht regelung auf temp value | 1 | 0 | LIGHT_CONTROL_ON_TEMP_VALUE_FLAG | 8223 | 201F | 153 | - | unsigned | 0 | 1 | 1
Relais Mode HB - Busy für Software! LB-Free | 0 | 0 | RELAIS_MODE | 8224 | 2020 | 154 | - | unsigned | 0 | 1 | 1
Factory Brightness Value | 1 | 0 | FACTORY_BRIGHTNESS_VALUE | 8225 | 2021 | 155 | lux | unsigned | 0 | 4000 | 1050
Alone At Work Mode = Bit 8-11 / Relais Mode = LB / Manual Initialisation = Bit 12-15 | 1 | 0 | ALONE_AT_WORK_RELAIS_MODE | 8226 | 2022 | 156 | - | unsigned | 0 | 257 | 257
Light Signalisation State Time - wie lange ist ein state / wenn = 0 - dann ist signalisation disabled | 1 | 0 | LIGHT_SIGNALISATION_STATE_TIME | 8227 | 2023 | 157 | ms | unsigned | 0 | 5000 | 700
User Set Point Sensor 1 | 1 | 0 | USER_BRIGHTNESS_VALUE | 8228 | 2024 | 158 | lux | unsigned | 0 | 4000 | 1050
User Set Point Sensor 2 | 1 | 0 | USER_BRIGHTNESS_VALUE_2 | 8229 | 2025 | 159 | lux | unsigned | 0 | 4000 | 1050
User Set Point Sensor 3 | 1 | 0 | USER_BRIGHTNESS_VALUE_3 | 8230 | 2026 | 160 | lux | unsigned | 0 | 4000 | 1050
User Set Point Sensor 4 | 1 | 0 | USER_BRIGHTNESS_VALUE_4 | 8231 | 2027 | 161 | lux | unsigned | 0 | 4000 | 1050
Burning duration LED Driver 1 [min] | 1 | 0 | BURNING_DURATION_LED_DRIVER_1 | 8232 | 2028 | 162 | min | unsigned | 0 | 65535 | 0
Burning duration LED Driver 2 [min] | 1 | 0 | BURNING_DURATION_LED_DRIVER_2 | 8233 | 2029 | 163 | min | unsigned | 0 | 65535 | 0
Burning duration LED Driver 3 [min] | 1 | 0 | BURNING_DURATION_LED_DRIVER_3 | 8234 | 202A | 164 | min | unsigned | 0 | 65535 | 0
Burning duration LED Driver 4 [min] | 1 | 0 | BURNING_DURATION_LED_DRIVER_4 | 8235 | 202B | 165 | min | unsigned | 0 | 65535 | 0
DALI Value summiert led driver 1 | 1 | 0 | BURNING_VALUE_SUMMED_LED_DRIVER_1 | 8236 | 202C | 166 | - | unsigned | 0 | 65535 | 0
DALI Value summiert led driver 2 | 1 | 0 | BURNING_VALUE_SUMMED_LED_DRIVER_2 | 8237 | 202D | 167 | - | unsigned | 0 | 65535 | 0
DALI Value summiert led driver 3 | 1 | 0 | BURNING_VALUE_SUMMED_LED_DRIVER_3 | 8238 | 202E | 168 | - | unsigned | 0 | 65535 | 0
DALI Value summiert led driver 4 | 1 | 0 | BURNING_VALUE_SUMMED_LED_DRIVER_4 | 8239 | 202F | 169 | - | unsigned | 0 | 65535 | 0
Overflow Burning Duration (LB) - HB = Overflow von Burning duration | 1 | 0 | OVERFLOW_DURATION_1 | 8240 | 2030 | 170 | - | unsigned | 0 | 65535 | 0
Overflow Burning Duration (LB) - HB = Overflow von Burning duration | 1 | 0 | OVERFLOW_DURATION_2 | 8241 | 2031 | 171 | - | unsigned | 0 | 65535 | 0
Overflow Burning Duration (LB) - HB = Overflow von Burning duration | 1 | 0 | OVERFLOW_DURATION_3 | 8242 | 2032 | 172 | - | unsigned | 0 | 65535 | 0
Overflow Burning Duration (LB) - HB = Overflow von Burning duration | 1 | 0 | OVERFLOW_DURATION_4 | 8243 | 2033 | 173 | - | unsigned | 0 | 65535 | 0
Overflow burning Value Summed | 1 | 0 | OVERFLOW_SUMMED_1 | 8244 | 2034 | 174 | - | unsigned | 0 | 65535 | 0
Overflow burning Value Summed | 1 | 0 | OVERFLOW_SUMMED_2 | 8245 | 2035 | 175 | - | unsigned | 0 | 65535 | 0
Overflow burning Value Summed | 1 | 0 | OVERFLOW_SUMMED_3 | 8246 | 2036 | 176 | - | unsigned | 0 | 65535 | 0
Overflow burning Value Summed | 1 | 0 | OVERFLOW_SUMMED_4 | 8247 | 2037 | 177 | - | unsigned | 0 | 65535 | 0
Number of Short Presses Input 1 | 1 | 0 | NUMBER_OF_SHORT_PRESSES_INPUT_1 | 8248 | 2038 | 178 | - | unsigned | 0 | 65535 | 0
Number of Long Presses Input 1 | 1 | 0 | NUMBER_OF_LONG_PRESSES_INPUT_1 | 8249 | 2039 | 179 | - | unsigned | 0 | 65535 | 0
Number of Short Presses Input 2 | 1 | 0 | NUMBER_OF_SHORT_PRESSES_INPUT_2 | 8250 | 203A | 180 | - | unsigned | 0 | 65535 | 0
Number of Long Presses Input 2 | 1 | 0 | NUMBER_OF_LONG_PRESSES_INPUT_2 | 8251 | 203B | 181 | - | unsigned | 0 | 65535 | 0
Last Multiklick Input 1 | 1 | 0 | LAST_MULTIKLICK_INPUT_1 | 8252 | 203C | 182 | - | unsigned | 0 | 65535 | 0
Last Multiklick Input 2 | 1 | 0 | LAST_MULTIKLICK_INPUT_2 | 8253 | 203D | 183 | - | unsigned | 0 | 65535 | 0
overvoltage value - count number of detected overvoltages and safe them in EEPROM | 1 | 0 | NUMBER_OF_AC_OVERVOLTAGE_DETECTED | 8254 | 203E | 184 | - | unsigned | 0 | 65535 | 0
Relais ON - OFF time HB = relais ON time LB = relais OFF time | 1 | 0 | RELAIS_PUSH_AND_RELEASE_TIME | 8255 | 203F | 185 | - | unsigned | 0 | 65535 | 1541
Error states Control Unit 1 = DALI short - 2 = Overvoltage - 3 = overcurrent N' - 4 = wrong sw on current Hardware - 5 = ??? | 1 | 0 | ERROR_STATES | 8256 | 2040 | 186 | - | unsigned | 0 | 65535 | 0
Short Press time - ms | 1 | 0 | TIME_SHORT_PRESS | 8257 | 2041 | 187 | ms | unsigned | 0 | 65535 | 500
Delay Press time - ms | 1 | 0 | TIME_DELAY_PRESS | 8258 | 2042 | 188 | ms | unsigned | 0 | 65535 | 200
long press time max | 1 | 0 | TIME_LONG_PRESS_MAX | 8259 | 2043 | 189 | ms | unsigned | 0 | 65535 | 60000
Parametrizing Press time | 1 | 0 | TIME_PARAMETRIZING_PRESS | 8260 | 2044 | 190 | ms | unsigned | 0 | 65535 | 20000
Sampling Time Dali Monitor (in minutes) | 1 | 0 | SAMPLING_TIME_DALI_MONITOR | 8261 | 2045 | 191 | min | unsigned | 0 | 65535 | 1
2nd Delay Time | 1 | 0 | SECOND_DELAY_TIME | 8262 | 2046 | 192 | [s] | unsigned | 0 | 65535 | 0
Luminaire Protected | 1 | 0 | LUMINAIRE_PROTECTED | 8263 | 2047 | 193 | - | unsigned | 0 | 65535 | 0
DALI2 Interface Protected (0 = not powered - 1 = powered) | 1 | 0 | DALI_2_INTERFACE_POWER | 8264 | 2048 | 194 | - | unsigned | 0 | 65535 | 0
AC Buttons Mode (bit[0] = AC1 - Enable or Disable bit[1] = AC2 - Enable or Disable | 1 | 0 | AC_BUTTONS_MODE | 8265 | 2049 | 195 | - | unsigned | 0 | 65535 | 0
Tunable Demo Mode Duration Day (sec) | 1 | 0 | TUNABLE_DEMO_MODE_DURATION_DAY | 8266 | 204A | 196 | s | unsigned | 0 | 65535 | 0
HB = CLM-Mode / LB = TIME_SYNC | 1 | 0 | CLM_MODE_TIME_SYNC | 8267 | 204B | 197 | - | unsigned | 0 | 65535 | 257
reserve6 | 1 | 0 | NOT_USED_6 | 8268 | 204C | 198 | - | unsigned | 0 | 65535 | 0
reserve7 | 1 | 0 | NOT_USED_7 | 8269 | 204D | 199 | - | unsigned | 0 | 65535 | 0
Time Zone | 1 | 0 | TIME_ZONE | 8270 | 204E | 200 | - | signed | 0 | 65535 | 1
Daylight Saving | 1 | 0 | DAYLIGHT_SAVING | 8271 | 204F | 201 | - | unsigned | 0 | 65535 | 1
Luminaire Type - Normal = 0 or Tuneable = 1 or ENEC = 2 | 1 | 0 | LUMINAIRE_TYPE | 10007 | 2717 | 202 | - | unsigned | 0 | 65535 | 0
Device states | 0 | 0 | DEVICE_STATES | 10008 | 2718 | 203 | - | unsigned | 0 | 65535 | 0
Device error states | 1 | 0 | DEVICE_ERROR_STATES | 10009 | 2719 | 204 | - | unsigned | 0 | 65535 | 0
luminaire temperature of leds | 0 | 0 | LUMINAIRE_TEMPERATURE | 10010 | 271A | 205 | K | unsigned | 0 | 65535 | 0
Relais Current IAC - no safe in eeprom | 0 | 0 | GET_MEASURED_IAC_NOUT | 13573 | 3505 | 206 | mA | unsigned | 0 | 65535 | 0
Get measured 3V3 | 0 | 0 | GET_MEASURED_3V3 | 16384 | 4000 | 207 | mV | unsigned | 0 | 65535 | 0
Get measured 12V | 0 | 0 | GET_MEASURED_12V | 16385 | 4001 | 208 | mV | unsigned | 0 | 65535 | 0
Get measured Current of 12V current | 0 | 0 | GET_MEASURED_12V_CURRENT | 16386 | 4002 | 209 | mV | unsigned | 0 | 65535 | 0
Get measured Current of 5V | 0 | 0 | GET_MEASURED_5V | 16387 | 4003 | 210 | mV | unsigned | 0 | 65535 | 0
Get measured Current of 18V | 0 | 0 | GET_MEASURED_18V | 16388 | 4004 | 211 | mV | unsigned | 0 | 65535 | 0
Get measured Modbus Voltage | 0 | 0 | GET_MEASURED_MODBUS_VOLTAGE | 16389 | 4005 | 212 | mV | unsigned | 0 | 65535 | 0
Get measured 230V IN | 0 | 0 | GET_MEASURED_VAC_IN | 16390 | 4006 | 213 | mV | unsigned | 0 | 65535 | 0
Get measured AIN Voltage | 0 | 0 | GET_MEASURED_AIN | 16391 | 4007 | 214 | mV | unsigned | 0 | 65535 | 0
Get measured temperature | 0 | 0 | GET_MEASURED_TEMPERATURE | 16392 | 4008 | 215 | Celsius | unsigned | 0 | 65535 | 0
ISYS Sense | 0 | 0 | GET_MEASURED_ISYS_SENSE | 16393 | 4009 | 216 | - | unsigned | 0 | 65535 | 0
MCU id | 0 | 0 | GET_MEASURED_MCU_ID | 16394 | 400A | 217 | - | unsigned | 0 | 65535 | 0
Temp Brightness Value Head 1 | 0 | 0 | SET_POINT_LIGHT_REGULATION_1 | 16395 | 400B | 218 | lux | unsigned | 0 | 4000 | 0
Temp Brightness Value Head 2 | 0 | 0 | SET_POINT_LIGHT_REGULATION_2 | 16396 | 400C | 219 | lux | unsigned | 0 | 4000 | 0
Temp Brightness Value Head 3 | 0 | 0 | SET_POINT_LIGHT_REGULATION_3 | 16397 | 400D | 220 | lux | unsigned | 0 | 4000 | 0
Temp Brightness Value Head 4 | 0 | 0 | SET_POINT_LIGHT_REGULATION_4 | 16398 | 400E | 221 | lux | unsigned | 0 | 4000 | 0
Dali Value Driver 1 | 0 | 0 | DALI_VALUE_LIGHT_DECK_1 | 16399 | 400F | 222 | dali | unsigned | 254 | 4000 | 0
Dali Value Driver 2 | 0 | 0 | DALI_VALUE_LIGHT_DECK_2 | 16400 | 4010 | 223 | dali | unsigned | 254 | 4000 | 0
Dali Value Driver 3 | 0 | 0 | DALI_VALUE_LIGHT_DECK_3 | 16401 | 4011 | 224 | dali | unsigned | 254 | 4000 | 0
Dali Value Driver 4 | 0 | 0 | DALI_VALUE_LIGHT_DECK_4 | 16402 | 4012 | 225 | dali | unsigned | 254 | 4000 | 0
Raw Data PushButton 1 | 0 | 0 | RAW_DATA_PUSHBUTTON_1 | 16896 | 4200 | 226 | - | unsigned | 0 | 65535 | 0
Raw Data PushButton 2 | 0 | 0 | RAW_DATA_PUSHBUTTON_2 | 16897 | 4201 | 227 | - | unsigned | 0 | 65535 | 0
number of sw timers = HB | 0 | 0 | SW_TIMERS_STACK_SIZE | 16898 | 4202 | 228 | - | unsigned | 0 | 65535 | 0
CONFIG_PANEL1_BUTTON_UP_SHORT_PRESS | 1 | 0 | CONFIG_PANEL1_BUTTON_UP_SHORT_PRESS | 17664 | 4500 | 229 | - | unsigned | 0 | 65535 | 0
CONFIG_PANEL1_BUTTON_UP_LONG_PRESS | 1 | 0 | CONFIG_PANEL1_BUTTON_UP_LONG_PRESS | 17665 | 4501 | 230 | - | unsigned | 0 | 65535 | 0
CONFIG_PANEL1_BUTTON_UP_DOUBLE_PRESS | 1 | 0 | CONFIG_PANEL1_BUTTON_UP_DOUBLE_PRESS | 17666 | 4502 | 231 | - | unsigned | 0 | 65535 | 0
CONFIG_PANEL1_BUTTON_MIDDLE_SHORT_PRESS | 1 | 0 | CONFIG_PANEL1_BUTTON_MIDDLE_SHORT_PRESS | 17667 | 4503 | 232 | - | unsigned | 0 | 65535 | 0
CONFIG_PANEL1_BUTTON_MIDDLE_LONG_PRESS | 1 | 0 | CONFIG_PANEL1_BUTTON_MIDDLE_LONG_PRESS | 17668 | 4504 | 233 | - | unsigned | 0 | 65535 | 0
CONFIG_PANEL1_BUTTON_MIDDLE_DOUBLE_PRESS | 1 | 0 | CONFIG_PANEL1_BUTTON_MIDDLE_DOUBLE_PRESS | 17669 | 4505 | 234 | - | unsigned | 0 | 65535 | 0
CONFIG_PANEL1_BUTTON_DOWN_SHORT_PRESS | 1 | 0 | CONFIG_PANEL1_BUTTON_DOWN_SHORT_PRESS | 17670 | 4506 | 235 | - | unsigned | 0 | 65535 | 0
CONFIG_PANEL1_BUTTON_DOWN_LONG_PRESS | 1 | 0 | CONFIG_PANEL1_BUTTON_DOWN_LONG_PRESS | 17671 | 4507 | 236 | - | unsigned | 0 | 65535 | 0
CONFIG_PANEL1_BUTTON_DOWN_DOUBLE_PRESS | 1 | 0 | CONFIG_PANEL1_BUTTON_DOWN_DOUBLE_PRESS | 17672 | 4508 | 237 | - | unsigned | 0 | 65535 | 0
CONFIG_PANEL2_BUTTON_UP_SHORT_PRESS | 1 | 0 | CONFIG_PANEL2_BUTTON_UP_SHORT_PRESS | 17673 | 4509 | 238 | - | unsigned | 0 | 65535 | 0
CONFIG_PANEL2_BUTTON_UP_LONG_PRESS | 1 | 0 | CONFIG_PANEL2_BUTTON_UP_LONG_PRESS | 17674 | 450A | 239 | - | unsigned | 0 | 65535 | 0
CONFIG_PANEL2_BUTTON_UP_DOUBLE_PRESS | 1 | 0 | CONFIG_PANEL2_BUTTON_UP_DOUBLE_PRESS | 17675 | 450B | 240 | - | unsigned | 0 | 65535 | 0
CONFIG_PANEL2_BUTTON_MIDDLE_SHORT_PRESS | 1 | 0 | CONFIG_PANEL2_BUTTON_MIDDLE_SHORT_PRESS | 17676 | 450C | 241 | - | unsigned | 0 | 65535 | 0
CONFIG_PANEL2_BUTTON_MIDDLE_LONG_PRESS | 1 | 0 | CONFIG_PANEL2_BUTTON_MIDDLE_LONG_PRESS | 17677 | 450D | 242 | - | unsigned | 0 | 65535 | 0
CONFIG_PANEL2_BUTTON_MIDDLE_DOUBLE_PRESS | 1 | 0 | CONFIG_PANEL2_BUTTON_MIDDLE_DOUBLE_PRESS | 17678 | 450E | 243 | - | unsigned | 0 | 65535 | 0
CONFIG_PANEL2_BUTTON_DOWN_SHORT_PRESS | 1 | 0 | CONFIG_PANEL2_BUTTON_DOWN_SHORT_PRESS | 17679 | 450F | 244 | - | unsigned | 0 | 65535 | 0
CONFIG_PANEL2_BUTTON_DOWN_LONG_PRESS | 1 | 0 | CONFIG_PANEL2_BUTTON_DOWN_LONG_PRESS | 17680 | 4510 | 245 | - | unsigned | 0 | 65535 | 0
CONFIG_PANEL2_BUTTON_DOWN_DOUBLE_PRESS | 1 | 0 | CONFIG_PANEL2_BUTTON_DOWN_DOUBLE_PRESS | 17681 | 4511 | 246 | - | unsigned | 0 | 65535 | 0
CONFIG_SENSORMODULE_BUTTON_SHORT_PRESS | 1 | 0 | CONFIG_SENSORMODULE_BUTTON_SHORT_PRESS | 17682 | 4512 | 247 | - | unsigned | 0 | 65535 | 0
CONFIG_SENSORMODULE_BUTTON_LONG_PRESS | 1 | 0 | CONFIG_SENSORMODULE_BUTTON_LONG_PRESS | 17683 | 4513 | 248 | - | unsigned | 0 | 65535 | 0
CONFIG_SENSORMODULE_BUTTON_DOUBLE_PRESS | 1 | 0 | CONFIG_SENSORMODULE_BUTTON_DOUBLE_PRESS | 17684 | 4514 | 249 | - | unsigned | 0 | 65535 | 0
CONFIG_AC_BUTTON_1_SHORT_PRESS | 1 | 0 | CONFIG_AC_BUTTON_1_SHORT_PRESS | 17685 | 4515 | 250 | - | unsigned | 0 | 65535 | 1537
CONFIG_AC_BUTTON_2_SHORT_PRESS | 1 | 0 | CONFIG_AC_BUTTON_2_SHORT_PRESS | 17686 | 4516 | 251 | - | unsigned | 0 | 65535 | 1538
CONFIG_AC_BUTTON_1_LONG_PRESS | 1 | 0 | CONFIG_AC_BUTTON_1_LONG_PRESS | 17687 | 4517 | 252 | - | unsigned | 0 | 65535 | 769
CONFIG_AC_BUTTON_2_LONG_PRESS | 1 | 0 | CONFIG_AC_BUTTON_2_LONG_PRESS | 17688 | 4518 | 253 | - | unsigned | 0 | 65535 | 770
CONFIG_AC_BUTTON_1_DOUBLE_PRESS | 1 | 0 | CONFIG_AC_BUTTON_1_DOUBLE_PRESS | 17689 | 4519 | 254 | - | unsigned | 0 | 65535 | 0
CONFIG_AC_BUTTON_2_DOUBLE_PRESS | 1 | 0 | CONFIG_AC_BUTTON_2_DOUBLE_PRESS | 17690 | 451A | 255 | - | unsigned | 0 | 65535 | 0
CONFIG_AC_BUTTON_1_TRIPPLE_PRESS | 1 | 0 | CONFIG_AC_BUTTON_1_TRIPPLE_PRESS | 17691 | 451B | 256 | - | unsigned | 0 | 65535 | 0
CONFIG_AC_BUTTON_2_TRIPPLE_PRESS | 1 | 0 | CONFIG_AC_BUTTON_2_TRIPPLE_PRESS | 17692 | 451C | 257 | - | unsigned | 0 | 65535 | 0
CONFIG_PANEL_1_EVENT_TO_TRIGGER | 1 | 0 | CONFIG_PANEL_1_EVENT_TO_TRIGGER | 17693 | 451D | 258 | - | unsigned | 0 | 65535 | 514
CONFIG_PANEL_2_EVENT_TO_TRIGGER | 1 | 0 | CONFIG_PANEL_2_EVENT_TO_TRIGGER | 17694 | 451E | 259 | - | unsigned | 0 | 65535 | 514
MANUEL_BRIGHTNESS_HEAD_1 | 0 | 0 | HEAD_1_MANUAL_BRIGHTNESS | 25091 | 6203 | 260 | DALI | unsigned | 0 | 65535 | 0
MANUEL_BRIGHTNESS_HEAD_2 | 0 | 0 | HEAD_2_MANUAL_BRIGHTNESS | 25347 | 6303 | 261 | DALI | unsigned | 0 | 65535 | 0
Status Head 1 (delaytime active?) | 0 | 0 | STATUS_HEAD_1 | 24582 | 6006 | 262 | - | unsigned | 0 | 65535 | 0
Status Head 2 (delaytime active?) | 0 | 0 | STATUS_HEAD_2 | 24583 | 6007 | 263 | - | unsigned | 0 | 65535 | 0
Status Head 3 (delaytime active?) | 0 | 0 | STATUS_HEAD_3 | 24584 | 6008 | 264 | - | unsigned | 0 | 65535 | 0
Status Head 4 (delaytime active?) | 0 | 0 | STATUS_HEAD_4 | 24585 | 6009 | 265 | - | unsigned | 0 | 65535 | 0
Firmware Update | 0 | 0 | FW_UPDATE | 20480 | 5000 | 266 | - | unsigned | 0 | 65535 | 0
Firmware Update 1 | 0 | 0 | FW_UPDATE_1 | 20481 | 5001 | 267 | - | unsigned | 0 | 65535 | 0
Firmware Update 2 | 0 | 0 | FW_UPDATE_2 | 20482 | 5002 | 268 | - | unsigned | 0 | 65535 | 0
Firmware Update 3 | 0 | 0 | FW_UPDATE_3 | 20483 | 5003 | 269 | - | unsigned | 0 | 65535 | 0
Firmware Update 4 | 0 | 0 | FW_UPDATE_4 | 20484 | 5004 | 270 | - | unsigned | 0 | 65535 | 0
Firmware Update 5 | 0 | 0 | FW_UPDATE_5 | 20485 | 5005 | 271 | - | unsigned | 0 | 65535 | 0
Firmware Update 6 | 0 | 0 | FW_UPDATE_6 | 20486 | 5006 | 272 | - | unsigned | 0 | 65535 | 0
Firmware Update 7 | 0 | 0 | FW_UPDATE_7 | 20487 | 5007 | 273 | - | unsigned | 0 | 65535 | 0
Firmware Update 8 | 0 | 0 | FW_UPDATE_8 | 20488 | 5008 | 274 | - | unsigned | 0 | 65535 | 0
Firmware Update 9 | 0 | 0 | FW_UPDATE_9 | 20489 | 5009 | 275 | - | unsigned | 0 | 65535 | 0
Firmware Update 10 | 0 | 0 | FW_UPDATE_10 | 20490 | 500A | 276 | - | unsigned | 0 | 65535 | 0
Firmware Update 11 | 0 | 0 | FW_UPDATE_11 | 20491 | 500B | 277 | - | unsigned | 0 | 65535 | 0
Firmware Update 12 | 0 | 0 | FW_UPDATE_12 | 20492 | 500C | 278 | - | unsigned | 0 | 65535 | 0
Firmware Update 13 | 0 | 0 | FW_UPDATE_13 | 20493 | 500D | 279 | - | unsigned | 0 | 65535 | 0
Firmware Update 14 | 0 | 0 | FW_UPDATE_14 | 20494 | 500E | 280 | - | unsigned | 0 | 65535 | 0
Firmware Update 15 | 0 | 0 | FW_UPDATE_15 | 20495 | 500F | 281 | - | unsigned | 0 | 65535 | 0
Firmware Update 16 | 0 | 0 | FW_UPDATE_16 | 20496 | 5010 | 282 | - | unsigned | 0 | 65535 | 0
Firmware Update 17 | 0 | 0 | FW_UPDATE_17 | 20497 | 5011 | 283 | - | unsigned | 0 | 65535 | 0
Firmware Update 18 | 0 | 0 | FW_UPDATE_18 | 20498 | 5012 | 284 | - | unsigned | 0 | 65535 | 0
Firmware Update 19 | 0 | 0 | FW_UPDATE_19 | 20499 | 5013 | 285 | - | unsigned | 0 | 65535 | 0
Firmware Update 20 | 0 | 0 | FW_UPDATE_20 | 20500 | 5014 | 286 | - | unsigned | 0 | 65535 | 0
Firmware Update 21 | 0 | 0 | FW_UPDATE_21 | 20501 | 5015 | 287 | - | unsigned | 0 | 65535 | 0
Firmware Update 22 | 0 | 0 | FW_UPDATE_22 | 20502 | 5016 | 288 | - | unsigned | 0 | 65535 | 0
Firmware Update 23 | 0 | 0 | FW_UPDATE_23 | 20503 | 5017 | 289 | - | unsigned | 0 | 65535 | 0
Firmware Update 24 | 0 | 0 | FW_UPDATE_24 | 20504 | 5018 | 290 | - | unsigned | 0 | 65535 | 0
Firmware Update 25 | 0 | 0 | FW_UPDATE_25 | 20505 | 5019 | 291 | - | unsigned | 0 | 65535 | 0
Firmware Update 26 | 0 | 0 | FW_UPDATE_26 | 20506 | 501A | 292 | - | unsigned | 0 | 65535 | 0
Firmware Update 27 | 0 | 0 | FW_UPDATE_27 | 20507 | 501B | 293 | - | unsigned | 0 | 65535 | 0
Firmware Update 28 | 0 | 0 | FW_UPDATE_28 | 20508 | 501C | 294 | - | unsigned | 0 | 65535 | 0
Firmware Update 29 | 0 | 0 | FW_UPDATE_29 | 20509 | 501D | 295 | - | unsigned | 0 | 65535 | 0
Firmware Update 30 | 0 | 0 | FW_UPDATE_30 | 20510 | 501E | 296 | - | unsigned | 0 | 65535 | 0
Firmware Update 31 | 0 | 0 | FW_UPDATE_31 | 20511 | 501F | 297 | - | unsigned | 0 | 65535 | 0
Firmware Update 32 | 0 | 0 | FW_UPDATE_32 | 20512 | 5020 | 298 | - | unsigned | 0 | 65535 | 0
Firmware Update 33 | 0 | 0 | FW_UPDATE_33 | 20513 | 5021 | 299 | - | unsigned | 0 | 65535 | 0
Firmware Update 34 | 0 | 0 | FW_UPDATE_34 | 20514 | 5022 | 300 | - | unsigned | 0 | 65535 | 0
Firmware Update 35 | 0 | 0 | FW_UPDATE_35 | 20515 | 5023 | 301 | - | unsigned | 0 | 65535 | 0
Firmware Update 36 | 0 | 0 | FW_UPDATE_36 | 20516 | 5024 | 302 | - | unsigned | 0 | 65535 | 0
Firmware Update 37 | 0 | 0 | FW_UPDATE_37 | 20517 | 5025 | 303 | - | unsigned | 0 | 65535 | 0
Firmware Update 38 | 0 | 0 | FW_UPDATE_38 | 20518 | 5026 | 304 | - | unsigned | 0 | 65535 | 0
Firmware Update 39 | 0 | 0 | FW_UPDATE_39 | 20519 | 5027 | 305 | - | unsigned | 0 | 65535 | 0
Firmware Update 40 | 0 | 0 | FW_UPDATE_40 | 20520 | 5028 | 306 | - | unsigned | 0 | 65535 | 0
Firmware Update 41 | 0 | 0 | FW_UPDATE_41 | 20521 | 5029 | 307 | - | unsigned | 0 | 65535 | 0
Firmware Update 42 | 0 | 0 | FW_UPDATE_42 | 20522 | 502A | 308 | - | unsigned | 0 | 65535 | 0
Firmware Update 43 | 0 | 0 | FW_UPDATE_43 | 20523 | 502B | 309 | - | unsigned | 0 | 65535 | 0
Firmware Update 44 | 0 | 0 | FW_UPDATE_44 | 20524 | 502C | 310 | - | unsigned | 0 | 65535 | 0
Firmware Update 45 | 0 | 0 | FW_UPDATE_45 | 20525 | 502D | 311 | - | unsigned | 0 | 65535 | 0
Firmware Update 46 | 0 | 0 | FW_UPDATE_46 | 20526 | 502E | 312 | - | unsigned | 0 | 65535 | 0
Firmware Update 47 | 0 | 0 | FW_UPDATE_47 | 20527 | 502F | 313 | - | unsigned | 0 | 65535 | 0
Firmware Update 48 | 0 | 0 | FW_UPDATE_48 | 20528 | 5030 | 314 | - | unsigned | 0 | 65535 | 0
Firmware Update 49 | 0 | 0 | FW_UPDATE_49 | 20529 | 5031 | 315 | - | unsigned | 0 | 65535 | 0
Firmware Update 50 | 0 | 0 | FW_UPDATE_50 | 20530 | 5032 | 316 | - | unsigned | 0 | 65535 | 0
Firmware Update 51 | 0 | 0 | FW_UPDATE_51 | 20531 | 5033 | 317 | - | unsigned | 0 | 65535 | 0
Firmware Update 52 | 0 | 0 | FW_UPDATE_52 | 20532 | 5034 | 318 | - | unsigned | 0 | 65535 | 0
Firmware Update 53 | 0 | 0 | FW_UPDATE_53 | 20533 | 5035 | 319 | - | unsigned | 0 | 65535 | 0
Firmware Update 54 | 0 | 0 | FW_UPDATE_54 | 20534 | 5036 | 320 | - | unsigned | 0 | 65535 | 0
Firmware Update 55 | 0 | 0 | FW_UPDATE_55 | 20535 | 5037 | 321 | - | unsigned | 0 | 65535 | 0
Firmware Update 56 | 0 | 0 | FW_UPDATE_56 | 20536 | 5038 | 322 | - | unsigned | 0 | 65535 | 0
Firmware Update 57 | 0 | 0 | FW_UPDATE_57 | 20537 | 5039 | 323 | - | unsigned | 0 | 65535 | 0
Firmware Update 58 | 0 | 0 | FW_UPDATE_58 | 20538 | 503A | 324 | - | unsigned | 0 | 65535 | 0
Firmware Update 59 | 0 | 0 | FW_UPDATE_59 | 20539 | 503B | 325 | - | unsigned | 0 | 65535 | 0
Firmware Update 60 | 0 | 0 | FW_UPDATE_60 | 20540 | 503C | 326 | - | unsigned | 0 | 65535 | 0
Firmware Update 61 | 0 | 0 | FW_UPDATE_61 | 20541 | 503D | 327 | - | unsigned | 0 | 65535 | 0
Firmware Update 62 | 0 | 0 | FW_UPDATE_62 | 20542 | 503E | 328 | - | unsigned | 0 | 65535 | 0
Firmware Update 63 | 0 | 0 | FW_UPDATE_63 | 20543 | 503F | 329 | - | unsigned | 0 | 65535 | 0
Firmware Update CRC Low Word | 0 | 0 | FW_UPDATE_CRC_LW | 20544 | 5040 | 330 | - | unsigned | 0 | 65535 | 0
Firmware Update CRC High Word | 0 | 0 | FW_UPDATE_CRC_HW | 20545 | 5041 | 331 | - | unsigned | 0 | 65535 | 0
Firmware Update State | 0 | 0 | FW_UPDATE_STATE | 20546 | 5042 | 332 | - | unsigned | 0 | 65535 | 0
Note on A74: Autor: MODBUS ADDRESS: Read and Write a user-specific or random generated modbus address
Note on A75: Autor: TIMEOUT: Modbus timeout after which a request is canceled (no response received in this time)
Note on A76: Autor: HIGHBYTE = COMMAND LOWBYTE = DEVICE TYPE Command 1 = Generate new random address Device Type 0 = Execute command on all device types Device Type >0 = Execute command only on devices with the same device type
Note on A77: Autor: 0x4578 = Flash Area 0x210 - 0x2FF is unlocked
Note on A122: Autor: [x, x , x , x][] 0=dalifinish 1=dali is busy 0=no Answer 1=dalianswer 0=no collision 1= collision not use // 0x 80 = dali busy // 0x 40 = dali answer // 0x 20 = Collison
Note on A157: Autor: HB: Busy by Software LB: bit 0: reserved for Relais Mode during Application @ Zero-Crossing: 0x02 = REL1 setzen 0x04 = REL1 löschen 0x06 = REL2 setzen 0x08 = REL2 löschen 0x0A = REL1+REL2 setzen 0x0C = REL1+REL2 löschen 0x12 = REL1 sofort setzen 0x14 = REL1 sofort löschen 0x16 = REL2 sofort setzen 0x18 = REL2 sofort löschen 0x1A = REL1 + REL2 sofort setzen 0x1C = REL1 + REL2 sofort löschen
Note on A206: Autor: Device states : MB-Addresse = 0x2718 / 10008 (Dez.) 0 = modbus off 1 = factory reset 2 = reset 3 = ModbusToDALI GateWay 4 = SlaveMode 5 = firmware update start 6 = fast Reset 7 = use HB 8 = manifacture Reset HB: 1 = modbus Power OFF 2 = modbus Power ON 3 = DA2_POWER_EN - ON 4 = DA_2_POWER_EN - OFF 5 = DA_PS Enable (ON) def. enabled 6 = DA_PS Disable (OFF) 7 = Enable 18V
Note on A207: LB: Counts, aufgewacht from watchdog (0-255) HB: free
Note on A208: LB: Counts, aufgewacht from watchdog (0-255) HB: free

## DiscreteInputs
#Name | Short-Name | MB-Adr (hex) | Index | Default
#Systemstatus
Zellspannung 1 ueberschreitet das obere Limit | C1OV | 1 | 0 | 0
Zellspannung 2 ueberschreitet das obere Limit | C2OV | 2 | 1 | 0
Zellspannung 3 ueberschreitet das obere Limit | C3OV | 3 | 2 | 0
Zellspannung 4 ueberschreitet das obere Limit | C4OV | 4 | 3 | 0
Zellspannung 5 ueberschreitet das obere Limit | C5OV | 5 | 4 | 0
Zellspannung 6 ueberschreitet das obere Limit | C6OV | 6 | 5 | 0
Zellspannung 7 ueberschreitet das obere Limit | C7OV | 7 | 6 | 0
Zellspannung 8 ueberschreitet das obere Limit | C8OV | 8 | 7 | 0
Zellspannung 9 ueberschreitet das obere Limit | C9OV | 9 | 8 | 0
Zellspannung 10 ueberschreitet das obere Limit | C10OV | 10 | 9 | 0
Zellspannung 11 ueberschreitet das obere Limit | C11OV | 11 | 10 | 0
Zellspannung 12 ueberschreitet das obere Limit | C12OV | 12 | 11 | 0
Zellspannung 13 ueberschreitet das obere Limit | C13OV | 13 | 12 | 0
Zellspannung 14 ueberschreitet das obere Limit | C14OV | 14 | 13 | 0
Zellspannung 15 ueberschreitet das obere Limit | C15OV | 15 | 14 | 0
Zellspannung 16 ueberschreitet das obere Limit | C16OV | 16 | 15 | 0
Zellspannung 17 ueberschreitet das obere Limit | C17OV | 17 | 16 | 0
Zellspannung 18 ueberschreitet das obere Limit | C18OV | 18 | 17 | 0
Zellspannung 19 ueberschreitet das obere Limit | C19OV | 19 | 18 | 0
Zellspannung 20 ueberschreitet das obere Limit | C20OV | 20 | 19 | 0
Zellspannung 21 ueberschreitet das obere Limit | C21OV | 21 | 20 | 0
Zellspannung 22 ueberschreitet das obere Limit | C22OV | 22 | 21 | 0
Zellspannung 23 ueberschreitet das obere Limit | C23OV | 23 | 22 | 0
Zellspannung 24 ueberschreitet das obere Limit | C24OV | 24 | 23 | 0
Zellspannung 1 unterschreitet das untere Limit | C1UV | 25 | 24 | 0
Zellspannung 2 unterschreitet das obere Limit | C2UV | 26 | 25 | 0
Zellspannung 3 unterschreitet das obere Limit | C3UV | 27 | 26 | 0
Zellspannung 4 unterschreitet das obere Limit | C4UV | 28 | 27 | 0
Zellspannung 5 unterschreitet das obere Limit | C5UV | 29 | 28 | 0
Zellspannung 6 unterschreitet das obere Limit | C6UV | 30 | 29 | 0
Zellspannung 7 unterschreitet das obere Limit | C7UV | 31 | 30 | 0
Zellspannung 8 unterschreitet das obere Limit | C8UV | 32 | 31 | 0
Zellspannung 9 unterschreitet das obere Limit | C9UV | 33 | 32 | 0
Zellspannung 10 unterschreitet das obere Limit | C10UV | 34 | 33 | 0
Zellspannung 11 unterschreitet das obere Limit | C11UV | 35 | 34 | 0
Zellspannung 12 unterschreitet das obere Limit | C12UV | 36 | 35 | 0
Zellspannung 13 unterschreitet das untere Limit | C13UV | 37 | 36 | 0
Zellspannung 14 unterschreitet das obere Limit | C14UV | 38 | 37 | 0
Zellspannung 15 unterschreitet das obere Limit | C15UV | 39 | 38 | 0
Zellspannung 16 unterschreitet das obere Limit | C16UV | 40 | 39 | 0
Zellspannung 17 unterschreitet das obere Limit | C17UV | 41 | 40 | 0
Zellspannung 18 unterschreitet das obere Limit | C18UV | 42 | 41 | 0
Zellspannung 19 unterschreitet das obere Limit | C19UV | 43 | 42 | 0
Zellspannung 20 unterschreitet das obere Limit | C20UV | 44 | 43 | 0
Zellspannung 21 unterschreitet das obere Limit | C21UV | 45 | 44 | 0
Zellspannung 22 unterschreitet das obere Limit | C22UV | 46 | 45 | 0
Zellspannung 23 unterschreitet das obere Limit | C23UV | 47 | 46 | 0
Zellspannung 24 unterschreitet das obere Limit | C24UV | 48 | 47 | 0
Die Gesamtbatteriespannung ueberschreitet das obere Limit | BATHIGH | 49 | 48 | 0
Die Gesamtbatteriespannung ueberschreitet das untere Limit | BATLOW | 50 | 49 | 0
Batterie wird aktuell entladen | DSG | 51 | 50 | 0
Die Batterie ist voll aufgeladen | FC | 52 | 51 | 0
Die Batteriekapazitaet unterschreitet die erste Warnschwelle | SOC1 | 53 | 52 | 0
Die Batteriekapazitaet unterschreitet die zweite finale Warnschwelle | SOCF | 54 | 53 | 0
Die Batterietemperatur ist ausserhalb des zulaessigen Bereichs fuer Ladung | CHG_INH | 55 | 54 | 0
uebertemperatur bei Laden | OTC | 56 | 55 | 0
(Schnell-)Laden erlaubt | CHG | 57 | 56 | 0
Internen Kurzschluss detektiert | ISD | 58 | 57 | 0
uebertemperatur bei Entladen | OTD | 59 | 58 | 0
#Geraetestatus
Error in bamo_modbus_vars | BAMO_MODBUS_VARS_ERR | 60 | 59 | 0
Error in modbus_slave_if | BAMO_MODBUS_SLAVE_IF_ERR | 61 | 60 | 0
Error in ltc6804_ctrl | BAMO_LTC6804_CTRL_ERR | 62 | 61 | 0
Error in bq34z110_ctrl | BAMO_BQ34Z110_CTRL_ERR | 63 | 62 | 0
Error in ntc_ctrl | BAMO_NTC_CTRL_ERR | 64 | 63 | 0
Error in modbus_serial | BAMO_MODBUS_SERIAL_ERR | 65 | 64 | 0
Error in ltc6804_spi | BAMO_LTC6804_SPI_ERR | 66 | 65 | 0
Error in bq34z110_i2c | BAMO_BQ34Z110_I2C_ERR | 67 | 66 | 0
Error in anain | BAMO_ANAIN_ERR | 68 | 67 | 0
Error in rst_ctrl | BAMO_RST_CTRL_ERR | 69 | 68 | 0

## Coils
#Name | Short-Name | MB-Adr (hex) | Index | Default
#
BaMo software reset | SW_RST | 0 | 0 | 0
Processor reset | PROC_RST | 1 | 1 | 0
BaMo system reset | SYS_RST | 2 | 2 | 0
BaMo factory reset | FCT_RST | 3 | 3 | 0
BaMo On/Off | ON_OFF | 4 | 4 | 1
#STOP