## Master
#Modbus Slave Nodes
#Bezeichnung der Modbus Slave Nodes

## Slave
#Modbus Slave
#Generelle Informationen
mySlaveDeviceType=4
mySlaveDeviceAddress=6

## Funktionen
BaMo MODBUS | Function | Sub-function | Supported | Note
Data access | Read Coils |  | Yes
| Read Discrete Inputs |  | Yes
| Read Holding Registers |  | Yes
| Read Input Register |  | Yes
| Write Single Coil |  | Yes
| Write Single Register |  | Yes
| Write Multiple Coils |  | Yes
| Write Multiple Registers |  | Yes
| Read/Write Multiple Registers |  | No
| Mask Write Register |  | No
| Read FIFO queue |  | No
Diagnostics | Read Exception Status |  | No
| Diagnostic | Return Query Data | Yes | loopback
|  | Restart Communications Option | No
|  | Return Diagnostic Register | No | diagnostic register to be defined
|  | Change ASCII Input Delimiter | No
|  | Force Listen Only Mode | Yes | no response to requests
|  | Clear Counters and Diagnostic Register | Yes
|  | Return Bus Message Count | Yes | Received frames total (Req, ack)
|  | Return Bus Communication Error Count | Yes | Received frames with CRC error
|  | Return Bus Exception Error Count | Yes | Anzahl exception responses von Slave
|  | Return Slave Message Count | Yes | Anzahl CRC-ok requests an slave incl. broadcasts.
|  | Return Slave No Response Count | Yes | Anzahl CRC-ok Req ohne response
|  | Return Slave NAK Count | Yes | Anzahl NAK exception responses
|  | Return Slave Busy Count | No
|  | Return Bus Character Overrun Count | No
|  | Clear Overrun Counter and Flag | No
| Get Com event counter |  | No | Status (idle, busy), com event counter
| Get Com Event Log |  | No | Status, com event counter, bus message count, 0..64 event bytes ( Receive Event, Send Event, Entered Listen Only Mode,Initiated Communication Restart
| Report Slave ID |  | No | slave ID, status, additional data
| Read device Identification |  | No
File record access | Read File record |  | No
| Write File record |  | No
Other | Encapsulated Interface Transport |  | No

## InputRegister
#Name | Short-Name | MB-Adr (hex) | Index | Einheit | Type | Default
#Ladezustand
Spezifizierte Batteriekapazitaet | DESIGN_CAPACITY | 1 | 0 | 10 mAh | unsigned | 0
Berechnete kompensierte Gesamtbatteriekapazitaet | FULL_CHARGE_CAPACITY | 2 | 1 | 10 mAh | unsigned | 0
Unkompensierte Gesamtkapazitaet | FULL_AVAILABLE_CAPACITY | 3 | 2 | 10 mAh | unsigned | 0
Momentaner Ladezustand in % von der berechneten Gesamtkapazitaet | STATE_OF_CHARGE | 4 | 3 | % | unsigned | 0
Momentan verfuegbare kompensierte Batteriekapazitaet | REMAINING_CAPACITY | 5 | 4 | 10 mAh | unsigned | 0
Momentan verfuegbare unkompensierte Batteriekapazitaet | NOMINAL_AVAILABLE_CAPACITY | 6 | 5 | 10 mAh | unsigned | 0
Momentan verfuegbare Restenergie | AVAILABLE_ENERGY | 7 | 6 | Wh | unsigned | 0
Momentan verfuegbare Restleistung | AVAILABLE_POWER | 8 | 7 | W | unsigned | 0
Restlaufzeit bei bestimmtem Entladestrom | ATRATE_TIME_TO_EMPTY | 9 | 8 | min | unsigned | 0
Restlaufzeit bei momentanem Entladestrom | TIME_TO_EMPTY | 10 | 9 | min | unsigned | 0
Restlaufzeit bei maximalem Entladestrom | MAX_LOAD_TIME_TO_EMPTY | 11 | 10 | min | unsigned | 0
Restlaufzeit bei Standby-Entladestrom | STANDBY_TIME_TO_EMPTY | 12 | 11 | min | unsigned | 0
Restlaufzeit bei durchschnittlicher Entladeleistung | TIME_TO_EMPTY_AT_CONSTANT_POWER | 13 | 12 | min | unsigned | 0
Restladezeit bei durchschnittlichem Entladestrom | TIME_TO_FULL | 14 | 13 | min | unsigned | 0
Spezifizierte Batteriekapazitaet vs. Berechnete Gesamtbatteriekapazitaet | STATE_OF_HEALTH | 15 | 14 | % | unsigned | 0
Statusinformationen vom TI BQ34Z110 | CONTROL_STATUS | 16 | 15 | # | unsigned | 0
#Spannung
Aktuelle Gesamtbatteriespannung | VOLTAGE | 17 | 16 | mV | unsigned | 0
Spannung Zelle 1 | VOLTAGE_CELL_1 | 18 | 17 | 0.1 mV | unsigned | 0
Spannung Zelle 2 | VOLTAGE_CELL_2 | 19 | 18 | 0.1 mV | unsigned | 0
Spannung Zelle 3 | VOLTAGE_CELL_3 | 20 | 19 | 0.1 mV | unsigned | 0
Spannung Zelle 4 | VOLTAGE_CELL_4 | 21 | 20 | 0.1 mV | unsigned | 0
Spannung Zelle 5 | VOLTAGE_CELL_5 | 22 | 21 | 0.1 mV | unsigned | 0
Spannung Zelle 6 | VOLTAGE_CELL_6 | 23 | 22 | 0.1 mV | unsigned | 0
Spannung Zelle 7 | VOLTAGE_CELL_7 | 24 | 23 | 0.1 mV | unsigned | 0
Spannung Zelle 8 | VOLTAGE_CELL_8 | 25 | 24 | 0.1 mV | unsigned | 0
Spannung Zelle 9 | VOLTAGE_CELL_9 | 26 | 25 | 0.1 mV | unsigned | 0
Spannung Zelle 10 | VOLTAGE_CELL_10 | 27 | 26 | 0.1 mV | unsigned | 0
Spannung Zelle 11 | VOLTAGE_CELL_11 | 28 | 27 | 0.1 mV | unsigned | 0
Spannung Zelle 12 | VOLTAGE_CELL_12 | 29 | 28 | 0.1 mV | unsigned | 0
Spannung Zelle 13 | VOLTAGE_CELL_13 | 30 | 29 | 0.1 mV | unsigned | 0
Spannung Zelle 14 | VOLTAGE_CELL_14 | 31 | 30 | 0.1 mV | unsigned | 0
Spannung Zelle 15 | VOLTAGE_CELL_15 | 32 | 31 | 0.1 mV | unsigned | 0
Spannung Zelle 16 | VOLTAGE_CELL_16 | 33 | 32 | 0.1 mV | unsigned | 0
Spannung Zelle 17 | VOLTAGE_CELL_17 | 34 | 33 | 0.1 mV | unsigned | 0
Spannung Zelle 18 | VOLTAGE_CELL_18 | 35 | 34 | 0.1 mV | unsigned | 0
Spannung Zelle 19 | VOLTAGE_CELL_19 | 36 | 35 | 0.1 mV | unsigned | 0
Spannung Zelle 20 | VOLTAGE_CELL_20 | 37 | 36 | 0.1 mV | unsigned | 0
Spannung Zelle 21 | VOLTAGE_CELL_21 | 38 | 37 | 0.1 mV | unsigned | 0
Spannung Zelle 22 | VOLTAGE_CELL_22 | 39 | 38 | 0.1 mV | unsigned | 0
Spannung Zelle 23 | VOLTAGE_CELL_23 | 40 | 39 | 0.1 mV | unsigned | 0
Spannung Zelle 24 | VOLTAGE_CELL_24 | 41 | 40 | 0.1 mV | unsigned | 0
Empfohlene Ladespannung [mV] | CHARGE_VOLTAGE | 42 | 41 | mV | unsigned | 0
#Strom
Durchschnittlicher Lade- bzw. Entladestrom | AVERAGE_CURRENT | 43 | 42 | 10 mA | signed | 0
Momentaner Lade- bzw. Entladestrom | CURRENT | 44 | 43 | 10 mA | signed | 0
Maximaler Entladestrom im aktuellen Ladezyklus | MAX_LOAD_CURRENT | 45 | 44 | 10 mA | signed | 0
Standby Strom | STANDBY_CURRENT | 46 | 45 | 10 mA | signed | 0
Durchschnittliche Entladeleistung | AVERAGE_POWER | 47 | 46 | W | unsigned | 0
Empfohlener Ladestrom | CHARGE_CURRENT | 48 | 47 | 10 mA | signed | 0
Schaetzung des Selbstentladestroms | SELF_DISCHARGE_CURRENT | 49 | 48 | 10 mA | signed | 0
Anzahl Entladezyklen | CYCLE_COUNT | 50 | 49 | # | unsigned | 0
#Temperatur
Temperaturmesswert NTC 1 (PC 0) | NTC_PC_0 | 51 | 50 | 0.01°C | signed | 0
Temperaturmesswert NTC 2 (PC 1) | NTC_PC_1 | 52 | 51 | 0.01°C | signed | 0
Temperaturmesswert NTC 3 (LTC 0) | NTC_LTC_0 | 53 | 52 | 0.01°C | signed | 0
Temperaturmesswert NTC 4 (LTC 1) | NTC_LTC_1 | 54 | 53 | 0.01°C | signed | 0
Temperaturmesswert NTC 5 (LTC 2) | NTC_LTC_2 | 55 | 54 | 0.01°C | signed | 0
Temperaturmesswert NTC 6 (BQZ) | NTC_BQZ | 56 | 55 | 0.01°C | signed | 0
#LTC6804
Gesamtspannung | LTC6804_SOC_1 | 57 | 56 | mV | unsigned | 0
Gesamtspannung | LTC6804_SOC_2 | 58 | 57 | mV | unsigned | 0
Analogspannung | LTC6804_VA_1 | 59 | 58 | 0.1 mV | unsigned | 0
Analogspannung | LTC6804_VA_2 | 60 | 59 | 0.1 mV | unsigned | 0
Digitalspannung | LTC6804_VD_1 | 61 | 60 | 0.1 mV | unsigned | 0
Digitalspannung | LTC6804_VD_2 | 62 | 61 | 0.1 mV | unsigned | 0
Referenzspannung U_ref2 | LTC6804_REF2_1 | 63 | 62 | 0.1 mV | unsigned | 0
Referenzspannung U_ref2 | LTC6804_REF2_2 | 64 | 63 | 0.1 mV | unsigned | 0
#DEVICE information
Manufacturer | DEV_MANUFACTURER | 65 | 64 | ASCII | unsigned | 83
Manufacturer 1 | DEV_MANUFACTURER_1 | 66 | 65 | ASCII | unsigned | 97
Manufacturer 2 | DEV_MANUFACTURER_2 | 67 | 66 | ASCII | unsigned | 117
Manufacturer 3 | DEV_MANUFACTURER_3 | 68 | 67 | ASCII | unsigned | 116
Manufacturer 4 | DEV_MANUFACTURER_4 | 69 | 68 | ASCII | unsigned | 101
Manufacturer 5 | DEV_MANUFACTURER_5 | 70 | 69 | ASCII | unsigned | 114
Manufacturer 6 | DEV_MANUFACTURER_6 | 71 | 70 | ASCII | unsigned | 32
Manufacturer 7 | DEV_MANUFACTURER_7 | 72 | 71 | ASCII | unsigned | 76
Manufacturer 8 | DEV_MANUFACTURER_8 | 73 | 72 | ASCII | unsigned | 116
Manufacturer 9 | DEV_MANUFACTURER_9 | 74 | 73 | ASCII | unsigned | 100
Manufacturer 10 | DEV_MANUFACTURER_10 | 75 | 74 | ASCII | unsigned | 0
Device Name | DEV_NAME | 76 | 75 | ASCII | unsigned | 66
Device Name 1 | DEV_NAME_1 | 77 | 76 | ASCII | unsigned | 97
Device Name 2 | DEV_NAME_2 | 78 | 77 | ASCII | unsigned | 77
Device Name 3 | DEV_NAME_3 | 79 | 78 | ASCII | unsigned | 111
Device Name 4 | DEV_NAME_4 | 80 | 79 | ASCII | unsigned | 0
Device Type | DEV_TYPE | 81 | 80 | # | unsigned | 1
Release Version | VERSION_RELEASE | 82 | 81 | # | unsigned | 1
Major Version | VERSION_MAJOR | 83 | 82 | # | unsigned | 0
Minor Version | VERSION_MINOR | 84 | 83 | # | unsigned | 1
Build | BUILD | 85 | 84 | ASCII | unsigned | 0
Build 1 | BUILD_1 | 86 | 85 | ASCII | unsigned | 0
Build 2 | BUILD_2 | 87 | 86 | ASCII | unsigned | 0
Build 3 | BUILD_3 | 88 | 87 | ASCII | unsigned | 0
Build 4 | BUILD_4 | 89 | 88 | ASCII | unsigned | 0
Build 5 | BUILD_5 | 90 | 89 | ASCII | unsigned | 0
Build 6 | BUILD_6 | 91 | 90 | ASCII | unsigned | 0
Build 7 | BUILD_7 | 92 | 91 | ASCII | unsigned | 0
Build 8 | BUILD_8 | 93 | 92 | ASCII | unsigned | 0
Build 9 | BUILD_9 | 94 | 93 | ASCII | unsigned | 0

## HoldingRegister
#Name | EEPROM | Master-Mirror | Short-Name | MB-Adr (dezimal) | MB-Adr (hex) | Index | Einheit | Type | Min | Max | Default
#Konfiguration
Firmware Version Application (ex: firmwareProject 'ea') | 0 | 0 | FW_VERSION | 0 | 0 | 0 | char | unsigned | 0 | 65535 | 0
Firmware Version Application (ex: firmwareProject 'sy') | 0 | 0 | FW_VERSION_1 | 1 | 1 | 1 | char | unsigned | 0 | 65535 | 0
Firmware Version Application (ex: firmwareProject 'to') | 0 | 0 | FW_VERSION_2 | 2 | 2 | 2 | char | unsigned | 0 | 65535 | 0
Firmware Version Application (ex: firmwareProject 'uc') | 0 | 0 | FW_VERSION_3 | 3 | 3 | 3 | char | unsigned | 0 | 65535 | 0
Firmware Version Application (ex: firmwareProject 'h '-'') | 0 | 0 | FW_VERSION_4 | 4 | 4 | 4 | char | unsigned | 0 | 65535 | 0
Firmware Version Application (ex: firmwareVersion [0 1]) | 0 | 0 | FW_VERSION_5 | 5 | 5 | 5 | char | unsigned | 0 | 65535 | 0
Firmware Version Application (ex: firmwareVersion ['.' 3]) | 0 | 0 | FW_VERSION_6 | 6 | 6 | 6 | char | unsigned | 0 | 65535 | 0
Firmware Version Application (ex: firmwareVersion [4 '.']) | 0 | 0 | FW_VERSION_7 | 7 | 7 | 7 | char | unsigned | 0 | 65535 | 0
Firmware Version Application (ex: firmwareBuild [0 1]) | 0 | 0 | FW_VERSION_8 | 8 | 8 | 8 | char | unsigned | 0 | 65535 | 0
Firmware Version Application (ex: gitCommit ['-' 0]) | 0 | 0 | FW_VERSION_9 | 9 | 9 | 9 | char | unsigned | 0 | 65535 | 0
Firmware Version Application (ex: gitCommit[1 2]) | 0 | 0 | FW_VERSION_10 | 10 | A | 10 | char | unsigned | 0 | 65535 | 0
Firmware Version Application (ex: gitCommit[3 4]) | 0 | 0 | FW_VERSION_11 | 11 | B | 11 | char | unsigned | 0 | 65535 | 0
Firmware Version Application (ex: gitCommit[5 6]) | 0 | 0 | FW_VERSION_12 | 12 | C | 12 | char | unsigned | 0 | 65535 | 0
Firmware Version Application (ex: gitCommit[7 '-']) | 0 | 0 | FW_VERSION_13 | 13 | D | 13 | char | unsigned | 0 | 65535 | 0
Firmware Version Application (ex: firmwareTarget [0 1]) | 0 | 0 | FW_VERSION_14 | 14 | E | 14 | char | unsigned | 0 | 65535 | 0
Firmware Version Application (ex: firmwareTarget [2]) | 0 | 0 | FW_VERSION_15 | 15 | F | 15 | char | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_16 | 16 | 10 | 16 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_17 | 17 | 11 | 17 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_18 | 18 | 12 | 18 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_19 | 19 | 13 | 19 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_20 | 20 | 14 | 20 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_21 | 21 | 15 | 21 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_22 | 22 | 16 | 22 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_23 | 23 | 17 | 23 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_24 | 24 | 18 | 24 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_25 | 25 | 19 | 25 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_26 | 26 | 1A | 26 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_27 | 27 | 1B | 27 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_28 | 28 | 1C | 28 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_29 | 29 | 1D | 29 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_30 | 30 | 1E | 30 | - | unsigned | 0 | 65535 | 0
Firmware Version Application | 0 | 0 | FW_VERSION_31 | 31 | 1F | 31 | - | unsigned | 0 | 65535 | 0
Hardware Version (ex: '1 5') | 0 | 0 | HW_VERSION | 48 | 30 | 32 | char | unsigned | 0 | 65535 | 0
Hardware Version (ex: '0 6') | 0 | 0 | HW_VERSION_1 | 49 | 31 | 33 | char | unsigned | 0 | 65535 | 0
Hardware Version (ex: '- 1') | 0 | 0 | HW_VERSION_2 | 50 | 32 | 34 | char | unsigned | 0 | 65535 | 0
Hardware Version (ex: 'v x') | 0 | 0 | HW_VERSION_3 | 51 | 33 | 35 | char | unsigned | 0 | 65535 | 0
Hardware Version (ex: 'x') | 0 | 0 | HW_VERSION_4 | 52 | 34 | 36 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader (ex: 'bl') | 0 | 0 | FW_VERSION_BL | 53 | 35 | 37 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader (ex: '_e') | 0 | 0 | FW_VERSION_BL_1 | 54 | 36 | 38 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader (ex: 'as') | 0 | 0 | FW_VERSION_BL_2 | 55 | 37 | 39 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader (ex: 'yt') | 0 | 0 | FW_VERSION_BL_3 | 56 | 38 | 40 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader (ex: 'ou') | 0 | 0 | FW_VERSION_BL_4 | 57 | 39 | 41 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader (ex: 'ch') | 0 | 0 | FW_VERSION_BL_5 | 58 | 3A | 42 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader (ex: ' '-'[0] ') | 0 | 0 | FW_VERSION_BL_6 | 59 | 3B | 43 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader (ex: [1 '.']) | 0 | 0 | FW_VERSION_BL_7 | 60 | 3C | 44 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader (ex: [3 4]) | 0 | 0 | FW_VERSION_BL_8 | 61 | 3D | 45 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader (ex: ['.' [0]]) | 0 | 0 | FW_VERSION_BL_9 | 62 | 3E | 46 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader (ex: [1 2]) | 0 | 0 | FW_VERSION_BL_10 | 63 | 3F | 47 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader (ex: ['-' 0]) | 0 | 0 | FW_VERSION_BL_11 | 64 | 40 | 48 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader (ex: [1 2]) | 0 | 0 | FW_VERSION_BL_12 | 65 | 41 | 49 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader (ex: [3 4]) | 0 | 0 | FW_VERSION_BL_13 | 66 | 42 | 50 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader (ex: [5 6]) | 0 | 0 | FW_VERSION_BL_14 | 67 | 43 | 51 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader (ex: [7 '-']) | 0 | 0 | FW_VERSION_BL_15 | 68 | 44 | 52 | char | unsigned | 0 | 65535 | 0
Firmware Version Bootloader (ex: [0 1]) | 0 | 0 | FW_VERSION_BL_16 | 69 | 45 | 53 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader (ex: [2]) | 0 | 0 | FW_VERSION_BL_17 | 70 | 46 | 54 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_18 | 71 | 47 | 55 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_19 | 72 | 48 | 56 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_20 | 73 | 49 | 57 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_21 | 74 | 4A | 58 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_22 | 75 | 4B | 59 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_23 | 76 | 4C | 60 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_24 | 77 | 4D | 61 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_25 | 78 | 4E | 62 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_26 | 79 | 4F | 63 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_27 | 80 | 50 | 64 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_28 | 81 | 51 | 65 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_29 | 82 | 52 | 66 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_30 | 83 | 53 | 67 | - | unsigned | 0 | 65535 | 0
Firmware Version Bootloader | 0 | 0 | FW_VERSION_BL_31 | 84 | 54 | 68 | - | unsigned | 0 | 65535 | 0
Eeprom Version | 1 | 1 | EEPROM_VERSION | 255 | FF | 69 | - | unsigned | 0 | 65535 | 43776
Device Type | 0 | 1 | DEVICE_TYPE | 256 | 100 | 70 | - | unsigned | 0 | 65535 | 4
(Read/Set) Modbus Address | 1 | 0 | MODBUS_ADDRESS | 257 | 101 | 71 | - | unsigned | 0 | 65535 | 6
Modbus Timeout | 1 | 0 | MODBUS_TIMEOUT_LIGHTMEASURING_MULTI_FAKTOR | 258 | 102 | 72 | - | unsigned | 0 | 65535 | 20
Command - Devicetype - Generate Random Address for Device Type | 0 | 0 | MODBUS_COMMAND | 259 | 103 | 73 | - | unsigned | 0 | 65535 | 0
Write Manufacture Information | 0 | 0 | WRITE_MANUFACTURE_INFO | 512 | 200 | 74 | - | unsigned | 0 | 65535 | 0
Manufacturer Serialnumber | 0 | 0 | SERIAL_NUMBER | 528 | 210 | 75 | char | unsigned | 0 | 65535 | 0
Manufacturer Serialnumber | 0 | 0 | SERIAL_NUMBER_1 | 529 | 211 | 76 | char | unsigned | 0 | 65535 | 0
Manufacturer Serialnumber | 0 | 0 | SERIAL_NUMBER_2 | 530 | 212 | 77 | char | unsigned | 0 | 65535 | 0
Manufacturer Serialnumber | 0 | 0 | SERIAL_NUMBER_3 | 531 | 213 | 78 | char | unsigned | 0 | 65535 | 0
Manufacturer Serialnumber | 0 | 0 | SERIAL_NUMBER_4 | 532 | 214 | 79 | char | unsigned | 0 | 65535 | 0
Manufacturer Serialnumber | 0 | 0 | SERIAL_NUMBER_5 | 533 | 215 | 80 | char | unsigned | 0 | 65535 | 0
Manufacturer Serialnumber | 0 | 0 | SERIAL_NUMBER_6 | 534 | 216 | 81 | char | unsigned | 0 | 65535 | 0
Manufacturer Serialnumber | 0 | 0 | SERIAL_NUMBER_7 | 535 | 217 | 82 | char | unsigned | 0 | 65535 | 0
Manufacturer Hardware Version (HW/BOM) | 0 | 0 | HW_BOM_VERSION | 536 | 218 | 83 | char | unsigned | 0 | 65535 | 0
Manufacturer Hardware Version (HW/BOM) | 0 | 0 | HW_BOM_VERSION_1 | 537 | 219 | 84 | char | unsigned | 0 | 65535 | 0
Manufacturer Hardware Version (HW/BOM) | 0 | 0 | HW_BOM_VERSION_2 | 538 | 21A | 85 | char | unsigned | 0 | 65535 | 0
Manufacturer Hardware Version (HW/BOM) | 0 | 0 | HW_BOM_VERSION_3 | 539 | 21B | 86 | char | unsigned | 0 | 65535 | 0
Manufacturer Hardware Version (HW/BOM) | 0 | 0 | HW_BOM_VERSION_4 | 540 | 21C | 87 | char | unsigned | 0 | 65535 | 0
Manufacturer Hardware Version (HW/BOM) | 0 | 0 | HW_BOM_VERSION_5 | 541 | 21D | 88 | char | unsigned | 0 | 65535 | 0
Manufacturer Hardware Version (HW/BOM) | 0 | 0 | HW_BOM_VERSION_6 | 542 | 21E | 89 | char | unsigned | 0 | 65535 | 0
Manufacturer Hardware Version (HW/BOM) | 0 | 0 | HW_BOM_VERSION_7 | 543 | 21F | 90 | char | unsigned | 0 | 65535 | 0
Manufacturer Date/Time | 0 | 0 | DATE | 544 | 220 | 91 | char | unsigned | 0 | 65535 | 0
Manufacturer Date/Time | 0 | 0 | DATE_1 | 545 | 221 | 92 | char | unsigned | 0 | 65535 | 0
Manufacturer Date/Time | 0 | 0 | DATE_2 | 546 | 222 | 93 | char | unsigned | 0 | 65535 | 0
Manufacturer Date/Time | 0 | 0 | DATE_3 | 547 | 223 | 94 | char | unsigned | 0 | 65535 | 0
Manufacturer Date/Time | 0 | 0 | DATE_4 | 548 | 224 | 95 | char | unsigned | 0 | 65535 | 0
Manufacturer Date/Time | 0 | 0 | DATE_5 | 549 | 225 | 96 | char | unsigned | 0 | 65535 | 0
Manufacturer Date/Time | 0 | 0 | DATE_6 | 550 | 226 | 97 | char | unsigned | 0 | 65535 | 0
Manufacturer Date/Time | 0 | 0 | DATE_7 | 551 | 227 | 98 | char | unsigned | 0 | 65535 | 0
Regent Item Number | 0 | 0 | REGENT_ITEM_NUMBER | 552 | 228 | 99 | char | unsigned | 0 | 65535 | 0
Regent Item Number | 0 | 0 | REGENT_ITEM_NUMBER_1 | 553 | 229 | 100 | char | unsigned | 0 | 65535 | 0
Regent Item Number | 0 | 0 | REGENT_ITEM_NUMBER_2 | 554 | 22A | 101 | char | unsigned | 0 | 65535 | 0
Regent Item Number | 0 | 0 | REGENT_ITEM_NUMBER_3 | 555 | 22B | 102 | char | unsigned | 0 | 65535 | 0
Regent Item Number | 0 | 0 | REGENT_ITEM_NUMBER_4 | 556 | 22C | 103 | char | unsigned | 0 | 65535 | 0
Regent Item Number | 0 | 0 | REGENT_ITEM_NUMBER_5 | 557 | 22D | 104 | char | unsigned | 0 | 65535 | 0
Regent Item Number | 0 | 0 | REGENT_ITEM_NUMBER_6 | 558 | 22E | 105 | char | unsigned | 0 | 65535 | 0
Regent Item Number | 0 | 0 | REGENT_ITEM_NUMBER_7 | 559 | 22F | 106 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER | 560 | 230 | 107 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER_1 | 561 | 231 | 108 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER_2 | 562 | 232 | 109 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER_3 | 563 | 233 | 110 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER_4 | 564 | 234 | 111 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER_5 | 565 | 235 | 112 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER_6 | 566 | 236 | 113 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER_7 | 567 | 237 | 114 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER_8 | 568 | 238 | 115 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER_9 | 569 | 239 | 116 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER_10 | 570 | 23A | 117 | char | unsigned | 0 | 65535 | 0
Regent Serial Number | 0 | 0 | REGENT_SERIAL_NUMBER_11 | 571 | 23B | 118 | char | unsigned | 0 | 65535 | 0
Enable-Disable / 0 = disabled 1 = enabled / [0] = pir - [1] button - [2] lux - [3] temp | 1 | 0 | ENABLE_DISABLE | 4608 | 1200 | 119 | - | unsigned | 0 | 65535 | 15
Desk in use parameters: time window 1 [s] (default = 5s) | 1 | 0 | DESK_IN_USE_WINDOW1 | 4864 | 1300 | 120 | s | unsigned | 0 | 65535 | 5
Desk in use parameters: time window 2 [s] (default = 10s) | 1 | 0 | DESK_IN_USE_WINDOW2 | 4865 | 1301 | 121 | s | unsigned | 0 | 65535 | 10
Holding time desk in use [s] | 1 | 0 | HOLDINGTIME_DESK_IN_USE | 4866 | 1302 | 122 | s | unsigned | 0 | 65535 | 180
PIR holding time [ms] | 1 | 0 | PIR_HOLDING_TIME | 4867 | 1303 | 123 | ms | unsigned | 0 | 65535 | 500
PIR filtered: PIR motion with holding time | 0 | 1 | MOTION_EVENT | 4868 | 1304 | 124 | - | unsigned | 0 | 65535 | 0
Button Events (Master has to reset Event. Event init pressed will only be set if during whole time brightness sensor is darkened down) | 0 | 1 | BUTTON_EVENTS | 4869 | 1305 | 125 | - | unsigned | 0 | 65535 | 0
Brightness calibrated 0 - 5000 [Lux/10] (0xFFFF = value not valid) | 0 | 1 | LUX_VALUE | 4870 | 1306 | 126 | 0.1*Lux | unsigned | 0 | 65535 | 65535
Brightness calibrated filtered 0 - 5000 [Lux/10] (0xFFFF = value not valid) | 0 | 1 | LUX_VALUE_FILTERED | 4871 | 1307 | 127 | 0.1*Lux | unsigned | 0 | 65535 | 65535
Set Flag after (Time button t-init - 3s) and LUX < 30 | 0 | 1 | FORCE_INIT | 4872 | 1308 | 128 | - | unsigned | 0 | 65535 | 0
Error Sensormodule / bit [0]: Error PIR - bit[1]: Error BUTTON - bit[2]: Error Brightness - bit[3]: Error Temp | 0 | 1 | ERROR_SENSORMODULE | 4873 | 1309 | 129 | - | unsigned | 0 | 65535 | 0
Desk in use | 0 | 1 | WORKING_EVENT | 4874 | 130A | 130 | - | unsigned | 0 | 65535 | 0
Time button t-short | 1 | 0 | TIME_SHORT_PRESS | 5120 | 1400 | 131 | ms | unsigned | 0 | 65535 | 500
Time button t-delay | 1 | 0 | TIME_DELAY_PRESS | 5121 | 1401 | 132 | ms | unsigned | 0 | 65535 | 200
Time button t-long_max | 1 | 0 | TIME_LONG_PRESS_MAX | 5122 | 1402 | 133 | ms | unsigned | 0 | 65535 | 60000
Time button t-parametrizingInit | 1 | 0 | TIME_PARAMETRIZING_INIT_PRESS | 5123 | 1403 | 134 | ms | unsigned | 0 | 65535 | 20000
Number of short Button Events | 1 | 0 | NUMBER_OF_S_BUTTON_ON_OFF_EVENTS | 5124 | 1404 | 135 | - | unsigned | 0 | 65535 | 0
Number of long Button Events | 1 | 0 | NUMBER_OF_L_BUTTON_ON_OFF_EVENTS | 5125 | 1405 | 136 | - | unsigned | 0 | 65535 | 0
Calibrating factor brightness [Lux] (will be set to default 125/250 in software) | 1 | 0 | LUX_CAL_FACTOR | 5376 | 1500 | 137 | - | unsigned | 0 | 65535 | 0
Calibrating offset brightness [Lux] | 1 | 0 | LUX_CAL_OFFSET | 5377 | 1501 | 138 | - | signed | -32768 | 32767 | 0
Factor for average measurement [Lux] | 1 | 0 | NR_MEASUREMENTS_LUX_CAL | 5378 | 1502 | 139 | - | unsigned | 0 | 65535 | 5
Head type (ASCII L - R - C) | 1 | 0 | HEAD_TYPE | 5379 | 1503 | 140 | - | unsigned | 0 | 65535 | 0
Color temperatur head LED 1 (ex. 3000) | 1 | 0 | HEAD_LED_COLOR_1 | 5380 | 1504 | 141 | - | unsigned | 0 | 65535 | 0
Color temperatur head LED 2 | 1 | 0 | HEAD_LED_COLOR_2 | 5381 | 1505 | 142 | - | unsigned | 0 | 65535 | 0
Max Brightness value (will be set to default 5000/10000 in software) | 0 | 0 | MAX_BRIGHTNESS_VALUE | 5382 | 1506 | 143 | - | unsigned | 0 | 65535 | 0
Temperature uController (0xFFFF = value not valid) | 0 | 0 | TEMP_MICROCONTROLLER | 5632 | 1600 | 144 | - | unsigned | 0 | 65535 | 65535
Temperatur ex. Temp sensor (0xFFFF = value not valid) | 0 | 0 | TEMP_EXT_SENSOR | 5633 | 1601 | 145 | - | unsigned | 0 | 65535 | 65535
Device states - 1 = factory reset (all param. Def.) 2 = Reset 6 = FastReset 8 = Manufacturer Reset (all param. Def. Exept. Calibration data) | 0 | 0 | DEVICE_STATES | 10008 | 2718 | 146 | - | unsigned | 0 | 65535 | 0
Device error states (LowByte: Number of occured watchdog (0-255) HighByte: none) | 1 | 0 | DEVICE_ERROR_STATES | 10009 | 2719 | 147 | - | unsigned | 0 | 65535 | 0
Raw signal PIR: 0 = detection - 1 = no detection | 0 | 0 | RAW_SIGNAL_PIR | 16384 | 4000 | 148 | - | unsigned | 0 | 65535 | 0
Button states - 0 = not pressed 1 = pressed (manufacturing test) | 0 | 0 | RAW_SIGNAL_BUTTON | 16385 | 4001 | 149 | - | unsigned | 0 | 65535 | 0
Raw AD value brightness: [AD-value 0…4085] (manufacturer test) | 0 | 0 | RAW_SIGNAL_BRIGHTNESS | 16386 | 4002 | 150 | - | unsigned | 0 | 65535 | 0
PIR TEST (manufacturer test) | 0 | 0 | PIR_TEST | 16387 | 4003 | 151 | - | unsigned | 0 | 65535 | 0
Get measured 3.3V (manufacturer test) | 0 | 0 | MEASURED_3_3V | 16388 | 4004 | 152 | mV | unsigned | 0 | 65535 | 0
Get measured 5V (manufacturer test) | 0 | 0 | MEASURED_5V | 16389 | 4005 | 153 | mV | unsigned | 0 | 65535 | 0
Set LED green (manufacturer test) | 0 | 0 | LED_GREEN | 16390 | 4006 | 154 | - | unsigned | 0 | 65535 | 0
Set LED red (manufacturer test) | 0 | 0 | LED_RED | 16391 | 4007 | 155 | - | unsigned | 0 | 65535 | 0
Set Output Pin PA7 (manufacturer test) | 0 | 0 | PIN_PA7 | 16392 | 4008 | 156 | - | unsigned | 0 | 65535 | 0
Firmware Update | 0 | 0 | FW_UPDATE | 20480 | 5000 | 157 | - | unsigned | 0 | 65535 | 0
Firmware Update 1 | 0 | 0 | FW_UPDATE_1 | 20481 | 5001 | 158 | - | unsigned | 0 | 65535 | 0
Firmware Update 2 | 0 | 0 | FW_UPDATE_2 | 20482 | 5002 | 159 | - | unsigned | 0 | 65535 | 0
Firmware Update 3 | 0 | 0 | FW_UPDATE_3 | 20483 | 5003 | 160 | - | unsigned | 0 | 65535 | 0
Firmware Update 4 | 0 | 0 | FW_UPDATE_4 | 20484 | 5004 | 161 | - | unsigned | 0 | 65535 | 0
Firmware Update 5 | 0 | 0 | FW_UPDATE_5 | 20485 | 5005 | 162 | - | unsigned | 0 | 65535 | 0
Firmware Update 6 | 0 | 0 | FW_UPDATE_6 | 20486 | 5006 | 163 | - | unsigned | 0 | 65535 | 0
Firmware Update 7 | 0 | 0 | FW_UPDATE_7 | 20487 | 5007 | 164 | - | unsigned | 0 | 65535 | 0
Firmware Update 8 | 0 | 0 | FW_UPDATE_8 | 20488 | 5008 | 165 | - | unsigned | 0 | 65535 | 0
Firmware Update 9 | 0 | 0 | FW_UPDATE_9 | 20489 | 5009 | 166 | - | unsigned | 0 | 65535 | 0
Firmware Update 10 | 0 | 0 | FW_UPDATE_10 | 20490 | 500A | 167 | - | unsigned | 0 | 65535 | 0
Firmware Update 11 | 0 | 0 | FW_UPDATE_11 | 20491 | 500B | 168 | - | unsigned | 0 | 65535 | 0
Firmware Update 12 | 0 | 0 | FW_UPDATE_12 | 20492 | 500C | 169 | - | unsigned | 0 | 65535 | 0
Firmware Update 13 | 0 | 0 | FW_UPDATE_13 | 20493 | 500D | 170 | - | unsigned | 0 | 65535 | 0
Firmware Update 14 | 0 | 0 | FW_UPDATE_14 | 20494 | 500E | 171 | - | unsigned | 0 | 65535 | 0
Firmware Update 15 | 0 | 0 | FW_UPDATE_15 | 20495 | 500F | 172 | - | unsigned | 0 | 65535 | 0
Firmware Update 16 | 0 | 0 | FW_UPDATE_16 | 20496 | 5010 | 173 | - | unsigned | 0 | 65535 | 0
Firmware Update 17 | 0 | 0 | FW_UPDATE_17 | 20497 | 5011 | 174 | - | unsigned | 0 | 65535 | 0
Firmware Update 18 | 0 | 0 | FW_UPDATE_18 | 20498 | 5012 | 175 | - | unsigned | 0 | 65535 | 0
Firmware Update 19 | 0 | 0 | FW_UPDATE_19 | 20499 | 5013 | 176 | - | unsigned | 0 | 65535 | 0
Firmware Update 20 | 0 | 0 | FW_UPDATE_20 | 20500 | 5014 | 177 | - | unsigned | 0 | 65535 | 0
Firmware Update 21 | 0 | 0 | FW_UPDATE_21 | 20501 | 5015 | 178 | - | unsigned | 0 | 65535 | 0
Firmware Update 22 | 0 | 0 | FW_UPDATE_22 | 20502 | 5016 | 179 | - | unsigned | 0 | 65535 | 0
Firmware Update 23 | 0 | 0 | FW_UPDATE_23 | 20503 | 5017 | 180 | - | unsigned | 0 | 65535 | 0
Firmware Update 24 | 0 | 0 | FW_UPDATE_24 | 20504 | 5018 | 181 | - | unsigned | 0 | 65535 | 0
Firmware Update 25 | 0 | 0 | FW_UPDATE_25 | 20505 | 5019 | 182 | - | unsigned | 0 | 65535 | 0
Firmware Update 26 | 0 | 0 | FW_UPDATE_26 | 20506 | 501A | 183 | - | unsigned | 0 | 65535 | 0
Firmware Update 27 | 0 | 0 | FW_UPDATE_27 | 20507 | 501B | 184 | - | unsigned | 0 | 65535 | 0
Firmware Update 28 | 0 | 0 | FW_UPDATE_28 | 20508 | 501C | 185 | - | unsigned | 0 | 65535 | 0
Firmware Update 29 | 0 | 0 | FW_UPDATE_29 | 20509 | 501D | 186 | - | unsigned | 0 | 65535 | 0
Firmware Update 30 | 0 | 0 | FW_UPDATE_30 | 20510 | 501E | 187 | - | unsigned | 0 | 65535 | 0
Firmware Update 31 | 0 | 0 | FW_UPDATE_31 | 20511 | 501F | 188 | - | unsigned | 0 | 65535 | 0
Firmware Update 32 | 0 | 0 | FW_UPDATE_32 | 20512 | 5020 | 189 | - | unsigned | 0 | 65535 | 0
Firmware Update 33 | 0 | 0 | FW_UPDATE_33 | 20513 | 5021 | 190 | - | unsigned | 0 | 65535 | 0
Firmware Update 34 | 0 | 0 | FW_UPDATE_34 | 20514 | 5022 | 191 | - | unsigned | 0 | 65535 | 0
Firmware Update 35 | 0 | 0 | FW_UPDATE_35 | 20515 | 5023 | 192 | - | unsigned | 0 | 65535 | 0
Firmware Update 36 | 0 | 0 | FW_UPDATE_36 | 20516 | 5024 | 193 | - | unsigned | 0 | 65535 | 0
Firmware Update 37 | 0 | 0 | FW_UPDATE_37 | 20517 | 5025 | 194 | - | unsigned | 0 | 65535 | 0
Firmware Update 38 | 0 | 0 | FW_UPDATE_38 | 20518 | 5026 | 195 | - | unsigned | 0 | 65535 | 0
Firmware Update 39 | 0 | 0 | FW_UPDATE_39 | 20519 | 5027 | 196 | - | unsigned | 0 | 65535 | 0
Firmware Update 40 | 0 | 0 | FW_UPDATE_40 | 20520 | 5028 | 197 | - | unsigned | 0 | 65535 | 0
Firmware Update 41 | 0 | 0 | FW_UPDATE_41 | 20521 | 5029 | 198 | - | unsigned | 0 | 65535 | 0
Firmware Update 42 | 0 | 0 | FW_UPDATE_42 | 20522 | 502A | 199 | - | unsigned | 0 | 65535 | 0
Firmware Update 43 | 0 | 0 | FW_UPDATE_43 | 20523 | 502B | 200 | - | unsigned | 0 | 65535 | 0
Firmware Update 44 | 0 | 0 | FW_UPDATE_44 | 20524 | 502C | 201 | - | unsigned | 0 | 65535 | 0
Firmware Update 45 | 0 | 0 | FW_UPDATE_45 | 20525 | 502D | 202 | - | unsigned | 0 | 65535 | 0
Firmware Update 46 | 0 | 0 | FW_UPDATE_46 | 20526 | 502E | 203 | - | unsigned | 0 | 65535 | 0
Firmware Update 47 | 0 | 0 | FW_UPDATE_47 | 20527 | 502F | 204 | - | unsigned | 0 | 65535 | 0
Firmware Update 48 | 0 | 0 | FW_UPDATE_48 | 20528 | 5030 | 205 | - | unsigned | 0 | 65535 | 0
Firmware Update 49 | 0 | 0 | FW_UPDATE_49 | 20529 | 5031 | 206 | - | unsigned | 0 | 65535 | 0
Firmware Update 50 | 0 | 0 | FW_UPDATE_50 | 20530 | 5032 | 207 | - | unsigned | 0 | 65535 | 0
Firmware Update 51 | 0 | 0 | FW_UPDATE_51 | 20531 | 5033 | 208 | - | unsigned | 0 | 65535 | 0
Firmware Update 52 | 0 | 0 | FW_UPDATE_52 | 20532 | 5034 | 209 | - | unsigned | 0 | 65535 | 0
Firmware Update 53 | 0 | 0 | FW_UPDATE_53 | 20533 | 5035 | 210 | - | unsigned | 0 | 65535 | 0
Firmware Update 54 | 0 | 0 | FW_UPDATE_54 | 20534 | 5036 | 211 | - | unsigned | 0 | 65535 | 0
Firmware Update 55 | 0 | 0 | FW_UPDATE_55 | 20535 | 5037 | 212 | - | unsigned | 0 | 65535 | 0
Firmware Update 56 | 0 | 0 | FW_UPDATE_56 | 20536 | 5038 | 213 | - | unsigned | 0 | 65535 | 0
Firmware Update 57 | 0 | 0 | FW_UPDATE_57 | 20537 | 5039 | 214 | - | unsigned | 0 | 65535 | 0
Firmware Update 58 | 0 | 0 | FW_UPDATE_58 | 20538 | 503A | 215 | - | unsigned | 0 | 65535 | 0
Firmware Update 59 | 0 | 0 | FW_UPDATE_59 | 20539 | 503B | 216 | - | unsigned | 0 | 65535 | 0
Firmware Update 60 | 0 | 0 | FW_UPDATE_60 | 20540 | 503C | 217 | - | unsigned | 0 | 65535 | 0
Firmware Update 61 | 0 | 0 | FW_UPDATE_61 | 20541 | 503D | 218 | - | unsigned | 0 | 65535 | 0
Firmware Update 62 | 0 | 0 | FW_UPDATE_62 | 20542 | 503E | 219 | - | unsigned | 0 | 65535 | 0
Firmware Update 63 | 0 | 0 | FW_UPDATE_63 | 20543 | 503F | 220 | - | unsigned | 0 | 65535 | 0
Firmware Update CRC Low Word | 0 | 0 | FW_UPDATE_CRC_LW | 20544 | 5040 | 221 | - | unsigned | 0 | 65535 | 0
Firmware Update CRC High Word | 0 | 0 | FW_UPDATE_CRC_HW | 20545 | 5041 | 222 | - | unsigned | 0 | 65535 | 0
Firmware Update State | 0 | 0 | FW_UPDATE_STATE | 20546 | 5042 | 223 | - | unsigned | 0 | 65535 | 0
Note on A35: Autor: HW Version 2: R26 = 0E --> 1601-1v2 HW Version 3: R26 = 12k --> 1601-1v3 HW Version 4: R26 = 33k --> 1601-1v4 HW Version 5: R26 = 68k --> 1601-1v5 HW Version 6: R26 = 180k --> 1601-1v6 HW Version 7: R26 = open --> 1601-1v7
Note on A74: Autor: MODBUS ADDRESS: Read and Write a user-specific or random generated modbus address
Note on A75: Autor: TIMEOUT: Modbus timeout after which a request is canceled (no response received in this time)
Note on A76: Autor: HIGHBYTE = COMMAND LOWBYTE = DEVICE TYPE Command 1 = Generate new random address Device Type 0 = Execute command on all device types Device Type >0 = Execute command only on devices with the same device type Example, Generate random Adrress for sensormodule (Device Type 4): 0x0104
Note on A77: Autor: Pattern "0xDEAD" will erease flash block Pattern "0xBEEF" will programm flash block with data from HR 0x210 - 0x2FF
Note on A123: Autor: Window 1 Window 2 ¦____________¦________________________¦______________________________________________________________________________________________________________________________________________________˃ Time [s] ^ ^ ^ PIR PIR PIR <-------------------------------------Holding time desk in use------------------------------------------> <-------------------------------------Holding time desk in use------------------------------------------> ______________________________¦͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞͞ ͞ ͞ ͞ ͞ ͞ ͞ ¦___________ Desk in use To detect if desk is in use, at least one PIR signal has to be detected in Window 1 and at least one PIR signal has to be detected in Window 2. Once in both Windows a PIR signal was detected, desk is in use as long as timer "Holding time desk in use" has not terminated. A single PIR signal will reset the timer "Holding time desk in use" value area Window 1: 1s . . .5s value area Window 1: 1s . . .15s
Note on A124: Autor: Window 1 Window 2 ¦____________¦________________________¦______________________________________________________________________________________________________________________________________________________˃ Time [s] ^ ^ ^ PIR PIR PIR <-------------------------------------Holding time desk in use------------------------------------------> <-------------------------------------Holding time desk in use------------------------------------------> ______________________________¦͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞ ͞͞ ͞ ͞ ͞ ͞ ͞ ͞ ¦___________ Desk in use To detect if desk is in use, at least one PIR signal has to be detected in Window 1 and at least one PIR signal has to be detected in Window 2. Once in both Windows a PIR signal was detected, desk is in use as long as timer "Holding time desk in use" has not terminated. A single PIR signal will reset the timer "Holding time desk in use" value area Window 1: 1s . . .5s value area Window 1: 1s . . .15s
Note on A128: Autor: neu: BUTTON_NO_EVENT = 0, BUTTON_SHORT_PRESS = 1, BUTTON_LONG_PRESS = 2, BUTTON_LONG_RELEASED = 3, BUTTON_DOUBLE_CLICK = 4, BUTTON_3x_CLICK = 5, BUTTON_4x_CLICK = 6, BUTTON_5x_CLICK = 7, BUTTON_6x_CLICK = 8, BUTTON_7x_CLICK = 9, BUTTON_8x_CLICK = 10, BUTTON_9x_CLICK = 11, BUTTON_PARAMETRIZING_INIT = 12, BUTTON_ERROR = 13, alt 0b1xxx xxxx ' xxxx xxxx = Event multi click (9x) 0bx1xx xxxx ' xxxx xxxx = Event multi click (8x) 0bxx1x xxxx ' xxxx xxxx = Event multi click (7x) 0bxxx1 xxxx ' xxxx xxxx = Event multi click (6x) 0bxxxx 1xxx ' xxxx xxxx = Event multi click (5x) 0bxxxx x1xx ' xxxx xxxx = Event multi click (4x) 0b xxxx xx1x ' xxxx xxxx = Event multi click (3x) 0b xxxx xxx1 ' xxxx xxxx = Event multi click (2x) 0b xxxx xxxx ' 1xxx xxxx = not used 0b xxxx xxxx ' x1xx xxxx = not used 0b xxxx xxxx ' xx1x xxxx = Event error (>60s) 0b xxxx xxxx ' xxx1 xxxx = not used 0b xxxx xxxx ' xxxx 1xxx = Event init / parametrisizing (20s) 0b xxxx xxxx ' xxxx x1xx = Event long pressed released 0b xxxx xxxx ' xxxx xx1x = Event long pressed 0b xxxx xxxx ' xxxx xxx1 = Event short pressed
Note on A140: Autor: Value devided by 1000 = calibrating factor. Example: 020F = 527/1000 = 0.527
Note on A142: Autor: Average Measurement brightness [Lux] n = number of Measurements, ready every 100ms Example: n = 10: average Measurement of the last 10 Measurements. (one n measurement is already pre filtered with more than one measurement)
Note on A154: Autor: 0 = PIR not ready (ready 2 sec after power up) 1 = PIR OK 2 = PIR fault

## DiscreteInputs
#Name | Short-Name | MB-Adr (hex) | Index | Default
#Systemstatus
Zellspannung 1 ueberschreitet das obere Limit | C1OV | 1 | 0 | 0
Zellspannung 2 ueberschreitet das obere Limit | C2OV | 2 | 1 | 0
Zellspannung 3 ueberschreitet das obere Limit | C3OV | 3 | 2 | 0
Zellspannung 4 ueberschreitet das obere Limit | C4OV | 4 | 3 | 0
Zellspannung 5 ueberschreitet das obere Limit | C5OV | 5 | 4 | 0
Zellspannung 6 ueberschreitet das obere Limit | C6OV | 6 | 5 | 0
Zellspannung 7 ueberschreitet das obere Limit | C7OV | 7 | 6 | 0
Zellspannung 8 ueberschreitet das obere Limit | C8OV | 8 | 7 | 0
Zellspannung 9 ueberschreitet das obere Limit | C9OV | 9 | 8 | 0
Zellspannung 10 ueberschreitet das obere Limit | C10OV | 10 | 9 | 0
Zellspannung 11 ueberschreitet das obere Limit | C11OV | 11 | 10 | 0
Zellspannung 12 ueberschreitet das obere Limit | C12OV | 12 | 11 | 0
Zellspannung 13 ueberschreitet das obere Limit | C13OV | 13 | 12 | 0
Zellspannung 14 ueberschreitet das obere Limit | C14OV | 14 | 13 | 0
Zellspannung 15 ueberschreitet das obere Limit | C15OV | 15 | 14 | 0
Zellspannung 16 ueberschreitet das obere Limit | C16OV | 16 | 15 | 0
Zellspannung 17 ueberschreitet das obere Limit | C17OV | 17 | 16 | 0
Zellspannung 18 ueberschreitet das obere Limit | C18OV | 18 | 17 | 0
Zellspannung 19 ueberschreitet das obere Limit | C19OV | 19 | 18 | 0
Zellspannung 20 ueberschreitet das obere Limit | C20OV | 20 | 19 | 0
Zellspannung 21 ueberschreitet das obere Limit | C21OV | 21 | 20 | 0
Zellspannung 22 ueberschreitet das obere Limit | C22OV | 22 | 21 | 0
Zellspannung 23 ueberschreitet das obere Limit | C23OV | 23 | 22 | 0
Zellspannung 24 ueberschreitet das obere Limit | C24OV | 24 | 23 | 0
Zellspannung 1 unterschreitet das untere Limit | C1UV | 25 | 24 | 0
Zellspannung 2 unterschreitet das obere Limit | C2UV | 26 | 25 | 0
Zellspannung 3 unterschreitet das obere Limit | C3UV | 27 | 26 | 0
Zellspannung 4 unterschreitet das obere Limit | C4UV | 28 | 27 | 0
Zellspannung 5 unterschreitet das obere Limit | C5UV | 29 | 28 | 0
Zellspannung 6 unterschreitet das obere Limit | C6UV | 30 | 29 | 0
Zellspannung 7 unterschreitet das obere Limit | C7UV | 31 | 30 | 0
Zellspannung 8 unterschreitet das obere Limit | C8UV | 32 | 31 | 0
Zellspannung 9 unterschreitet das obere Limit | C9UV | 33 | 32 | 0
Zellspannung 10 unterschreitet das obere Limit | C10UV | 34 | 33 | 0
Zellspannung 11 unterschreitet das obere Limit | C11UV | 35 | 34 | 0
Zellspannung 12 unterschreitet das obere Limit | C12UV | 36 | 35 | 0
Zellspannung 13 unterschreitet das untere Limit | C13UV | 37 | 36 | 0
Zellspannung 14 unterschreitet das obere Limit | C14UV | 38 | 37 | 0
Zellspannung 15 unterschreitet das obere Limit | C15UV | 39 | 38 | 0
Zellspannung 16 unterschreitet das obere Limit | C16UV | 40 | 39 | 0
Zellspannung 17 unterschreitet das obere Limit | C17UV | 41 | 40 | 0
Zellspannung 18 unterschreitet das obere Limit | C18UV | 42 | 41 | 0
Zellspannung 19 unterschreitet das obere Limit | C19UV | 43 | 42 | 0
Zellspannung 20 unterschreitet das obere Limit | C20UV | 44 | 43 | 0
Zellspannung 21 unterschreitet das obere Limit | C21UV | 45 | 44 | 0
Zellspannung 22 unterschreitet das obere Limit | C22UV | 46 | 45 | 0
Zellspannung 23 unterschreitet das obere Limit | C23UV | 47 | 46 | 0
Zellspannung 24 unterschreitet das obere Limit | C24UV | 48 | 47 | 0
Die Gesamtbatteriespannung ueberschreitet das obere Limit | BATHIGH | 49 | 48 | 0
Die Gesamtbatteriespannung ueberschreitet das untere Limit | BATLOW | 50 | 49 | 0
Batterie wird aktuell entladen | DSG | 51 | 50 | 0
Die Batterie ist voll aufgeladen | FC | 52 | 51 | 0
Die Batteriekapazitaet unterschreitet die erste Warnschwelle | SOC1 | 53 | 52 | 0
Die Batteriekapazitaet unterschreitet die zweite finale Warnschwelle | SOCF | 54 | 53 | 0
Die Batterietemperatur ist ausserhalb des zulaessigen Bereichs fuer Ladung | CHG_INH | 55 | 54 | 0
uebertemperatur bei Laden | OTC | 56 | 55 | 0
(Schnell-)Laden erlaubt | CHG | 57 | 56 | 0
Internen Kurzschluss detektiert | ISD | 58 | 57 | 0
uebertemperatur bei Entladen | OTD | 59 | 58 | 0
#Geraetestatus
Error in bamo_modbus_vars | BAMO_MODBUS_VARS_ERR | 60 | 59 | 0
Error in modbus_slave_if | BAMO_MODBUS_SLAVE_IF_ERR | 61 | 60 | 0
Error in ltc6804_ctrl | BAMO_LTC6804_CTRL_ERR | 62 | 61 | 0
Error in bq34z110_ctrl | BAMO_BQ34Z110_CTRL_ERR | 63 | 62 | 0
Error in ntc_ctrl | BAMO_NTC_CTRL_ERR | 64 | 63 | 0
Error in modbus_serial | BAMO_MODBUS_SERIAL_ERR | 65 | 64 | 0
Error in ltc6804_spi | BAMO_LTC6804_SPI_ERR | 66 | 65 | 0
Error in bq34z110_i2c | BAMO_BQ34Z110_I2C_ERR | 67 | 66 | 0
Error in anain | BAMO_ANAIN_ERR | 68 | 67 | 0
Error in rst_ctrl | BAMO_RST_CTRL_ERR | 69 | 68 | 0

## Coils
#Name | Short-Name | MB-Adr (hex) | Index | Default
#
BaMo software reset | SW_RST | 0 | 0 | 0
Processor reset | PROC_RST | 1 | 1 | 0
BaMo system reset | SYS_RST | 2 | 2 | 0
BaMo factory reset | FCT_RST | 3 | 3 | 0
BaMo On/Off | ON_OFF | 4 | 4 | 1
#STOP